## Table H.2 & 20 - Excec Summary
Source: | \Data\Exceedence Files\2014 Wind Integration Study - 2012 Exceedance_All Months_Final.xlsx
\Data\Exceedence Files\2014 Wind Integration Study - 2013 Exceedance_All Months_Final.xlsx
Table H.2 Average Annual Regulating Margin Reserves, 2011 – 2013 (MW)
Year | Reserve Component | West BAA | East BAA | Combined
2011 | Load-Only Regulating Margin | 147.2397 | 246.8814 | 394.1212
(2012 WIS) | Incremental Wind Regulating Margin | 54.4376 | 130.8955 | 185.3331
| Total Regulating Margin | 201.6773 | 377.777 | 579.4543
| Wind Capacity | 589 | 1536 | 2126
2012 | Load-Only Regulating Margin | 140.8078 | 259.2856 | 400.0934
| Incremental Wind Regulating Margin | 76.5407 | 129.0118 | 205.5525
| Total Regulating Margin | 217.3486 | 388.2973 | 605.6459
| Wind Capacity | 785 | 1759 | 2543
2013 | Load-Only Regulating Margin | 166.1893 | 274.6495 | 440.8387
(2014 WIS) | Incremental Wind Regulating Margin | 55.4248 | 130.1615 | 185.5862
| Total Regulating Margin | 221.614 | 404.8109 | 626.425
| Wind Capacity | 785 | 1759 | 2543
Table H.20 - Regulating Margin Requirements Calculated for PacifiCorp’s System (MW)
Year | Reserve Component | West BAA | East BAA | Ramp | Combined
2011 | Load-Only Regulating Reserves | 99 | 176 | 119 | 394
(2012 WIS) | Incremental Wind Reserves | 50 | 126 | 9 | 185
| Total Reserves | 149 | 302 | 128 | 579
2012 | Load-Only Regulating Reserves | 95 | 186 | 119 | 400
| Incremental Wind Reserves | 71 | 123 | 11 | 206
| Total Reserves | 166 | 309 | 130 | 606
2013 | Load-Only Regulating Reserves | 119 | 203 | 119 | 441
(2013 WIS) | Incremental Wind Reserves | 51 | 123 | 12 | 186
| Total Reserves | 169 | 326 | 131 | 626

## Tbl H.3,14,21
Source: | Tbl H.15,19 - WI_Study Cost Results.xlsx
Table H.3- Wind Integration Cost, $/MWh
| 2012 WIS | 2014 WIS
| 2012$ | 2015$
Intra-hour Reserve | 2.19 | 2.35
Inter-hour/System Balancing | 0.36 | 0.71
Total Wind Integration | 2.55 | 3.06
Table H.14 - 2014 Wind Integration Costs
2014 WIS (2015$)
Intra-hour Reserve ($/MWh) | 2.35
Inter-hour/System Balancing ($/MWh) | 0.71
Total Wind Integration ($/MWh) | 3.06
Table H.21 – 2014 WIS Wind Integration Costs as Compared to 2012 WIS, $/MWh
| 2012 WIS | 2014 WIS
| (2012$) | (2015$)
Intra-hour Reserve ($/MWh) | 2.19 | 2.35
Inter-hour/System Balancing ($/MWh) | 0.36 | 0.71
Total Wind Integration ($/MWh) | 2.55 | 3.06

## Table H.4 2014 WIS Plants
Source: | \Data\Source Data\Wind Plant Capacity Comparison 2012 WIS vs. 2014 WIS.xlsx
Table H.4 - Historical Wind Production and Laod Data Inventory
| Nameplate Capacity | Beginning of Data | End of Data | Location
Wind Plants within PacifiCorp BAAs
Chevron Wind | 16.5 | 2012-01-01 | 2013-12-31 23:50 | East
Combine Hills | 41 | 2012-01-01 | 2013-12-31 23:50 | West
Dunlap 1 Wind | 111 | 2012-01-01 | 2013-12-31 23:50 | East
Five Pine and North Point | 119.7 | 2012-12-01 | 2013-12-31 23:50 | East
Foot Creek Generation | 85.0737 | 2012-01-01 | 2013-12-31 23:50 | East
Glenrock III Wind | 39 | 2012-01-01 | 2013-12-31 23:50 | East
Glenrock Wind | 99 | 2012-01-01 | 2013-12-31 23:50 | East
Goodnoe Hills Wind | 94 | 2012-01-01 | 2013-12-31 23:50 | West
High Plains Wind | 99 | 2012-01-01 | 2013-12-31 23:50 | East
Leaning Juniper 1 | 100.5 | 2012-01-01 | 2013-12-31 23:50 | West
Marengo I | 140.4 | 2012-01-01 | 2013-12-31 23:50 | West
Marengo II | 70.2 | 2012-01-01 | 2013-12-31 23:50 | West
McFadden Ridge Wind | 28.5 | 2012-01-01 | 2013-12-31 23:50 | East
Mountain Wind 1 QF | 60.9 | 2012-01-01 | 2013-12-31 23:50 | East
Mountain Wind 2 QF | 79.8 | 2012-01-01 | 2013-12-31 23:50 | East
Power County North and Power County South | 45 | 2012-01-01 | 2013-12-31 23:50 | East
Oregon Wind Farm QF | 64.55 | 2012-01-01 | 2013-12-31 23:50 | West
Rock River I | 49 | 2012-01-01 | 2013-12-31 23:50 | East
Rolling Hills Wind | 99 | 2012-01-01 | 2013-12-31 23:50 | East
Seven Mile Wind | 99 | 2012-01-01 | 2013-12-31 23:50 | East
Seven Mile II Wind | 19.5 | 2012-01-01 | 2013-12-31 23:50 | East
Spanish Fork Wind 2 QF | 18.9 | 2012-01-01 | 2013-12-31 23:50 | East
Stateline Contracted Generation | 175 | 2012-01-01 | 2013-12-31 23:50 | West
Three Buttes Wind | 99 | 2012-01-01 | 2013-12-31 23:50 | East
Top of the World Wind | 200.2 | 2012-01-01 | 2013-12-31 23:50 | East
Wolverine Creek | 64.5 | 2012-01-01 | 2013-12-31 23:50 | East
Long Hollow Wind |  | 2012-01-01 | 2013-12-31 23:50 | East
Campbell Wind |  | 2012-01-01 | 2013-12-31 23:50 | West
Horse Butte |  | 2012-06-19 08:40 | 2013-12-31 23:50 | East
Jolly Hills 1 |  | 2012-01-01 | 2013-12-31 23:50 | East
Jolly Hills 2 |  | 2012-01-01 | 2013-12-31 23:50 | East
Load Data
PACW Load |  | 2012-01-01 | 2013-12-31 23:50 | West
PACE Load |  | 2012-01-01 | 2013-12-31 23:50 | East

## Table H.5 Data Anomalies
Source: | \Data\Source Data\Load Source Data.xlsx
\Data\Source Data\Original Load Source Data.xlsx
Table H.5 - Examples of Load Data Anomalies and their Interpolated Solutions
Time | Original Load Value (MW) | Final Load Value (MW) | Method to Calculate Final Load Value
2012-01-05 12:20 | 5805.3663 | 5805.3663
2012-01-05 12:30 | 5211.0545 | 5793.1128 | 12:20 + 1/5 of (13:10 minus 12:20)
2012-01-05 12:40 | 5073.7945 | 5780.8594 | 12:20 + 2/5 of (13:10 minus 12:20)
2012-01-05 12:50 | 5062.6259 | 5768.6059 | 12:20 + 3/5 of (13:10 minus 12:20)
2012-01-05 13:00 | 5464.9335 | 5756.3524 | 12:20 + 4/5 of (13:10 minus 12:20)
2012-01-05 13:10 | 5744.0989 | 5744.0989
2013-05-06 08:50 | 5651.2803 | 5651.2803
2013-05-06 09:00 | 4582.5774 | 5694.3269 | Average of 8:50 and 9:10
2013-05-06 09:10 | 5737.3735 | 5737.3735

## Table H.6 Bins & Table H.7
Source: | \Data\Load Regulating\2014 Study Load Regulation 06-JUN.xlsm
Table H.7 - Recorded Interval Load Regulating Forecats and their Respective Deviations for |  |  |  | Table H.6 - Percentiles Dividing the June 2013 East Load Regulating
June 2013 Operational Data from PACE |  |  |  | Forecasts into 20 Bins
Date/Time | Load Regulation Forecast | Load Regulation Deviation | Bin Assignment | East
2013-06-01 06:00 | 4754.751 | 88.2089 | 20 | Bin Number | Percentile | Load Forecast
2013-06-01 06:10 | 4706.3663 | -66.8766 | 20 |  | MAX | 8586.7756
2013-06-01 06:20 | 4746.1906 | -12.6765 | 20 | 1 | 0.95 | 7869.3868
2013-06-01 06:30 | 4786.0149 | -35.8991 | 20 | 2 | 0.9 | 7474.6269
2013-06-01 06:40 | 4825.8391 | -25.9326 | 20 | 3 | 0.85 | 7220.0025
2013-06-01 06:50 | 4865.6634 | -46.0411 | 20 | 4 | 0.8 | 6983.6955
2013-06-01 07:00 | 4905.4877 | -46.2263 | 19 | 5 | 0.75 | 6806.575
2013-06-01 07:10 | 4983.9433 | 4.3633 | 19 | 6 | 0.7 | 6621.2183
2013-06-01 07:20 | 5016.1726 | -7.9751 | 18 | 7 | 0.65 | 6482.0197
2013-06-01 07:30 | 5048.4019 | -10.1188 | 18 | 8 | 0.6 | 6382.6204
2013-06-01 07:40 | 5080.6312 | 15.9922 | 18 | 9 | 0.55 | 6284.8667
2013-06-01 07:50 | 5112.8605 | 31.1402 | 18 | 10 | 0.5 | 6158.2436
2013-06-01 08:00 | 5145.0898 | 12.0005 | 17 | 11 | 0.45 | 6022.6944
2013-06-01 08:10 | 5157.5871 | 15.6975 | 17 | 12 | 0.4 | 5850.3599
2013-06-01 08:20 | 5182.0849 | -22.1826 | 17 | 13 | 0.35 | 5720.1033
2013-06-01 08:30 | 5206.5827 | -5.9035 | 17 | 14 | 0.3 | 5568.4241
2013-06-01 08:40 | 5231.0805 | 4.4465 | 17 | 15 | 0.25 | 5404.2868
2013-06-01 08:50 | 5255.5783 | 18.3076 | 17 | 16 | 0.2 | 5274.9644
2013-06-01 09:00 | 5280.0762 | 9.8803 | 16 | 17 | 0.15 | 5133.5562
2013-06-01 09:10 | 5278.3609 | -30.1921 | 16 | 18 | 0.1 | 5005.089
2013-06-01 09:20 | 5286.526 | 11.1549 | 16 | 19 | 0.05 | 4891.6468
2013-06-01 09:30 | 5294.691 | 2.4503 | 16 | 20 | MIN | 4521.4388
2013-06-01 09:40 | 5302.8561 | 24.9372 | 16
2013-06-01 09:50 | 5311.0211 | -3.8 | 16

## Fig H.6 EastData - Histogram
Source: | \Data\Load Regulating\2014 Study Load Regulation 06-JUN.xlsm
Figure H.6 - Histogram of Deviations Occurring about a June 2013 PACE Laod Regulating Forecast between 5,568 MW and 5,720 MW (bin 14)
Sum |  | -1337.4379 | -5837.1136 | -1419.627 | -1145.9369 | -1214.9369 | -3910.9452 | -2310.8587 | -2690.4776 | -1710.8739 | -5495.7162 | -6041.2628 | -2449.522 | 2046.0303 | 4249.3795 | 2593.9084 | 3506.016 | 4024.3741 | 4061.7099 | 3426.3015 | 1605.8107 | -5.4227
Comparison |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
Reg Down | 215.1685 | 261.0838 | 182.8268 | 189.4938 | 221.6433 | 270.7979 | 253.0667 | 213.082 | 164.1676 | 142.6396 | 158.0261 | 260.2856 | 448.1087 | 430.5643 | 353.1672 | 230.605 | 104.2477 | 124.5642 | 110.5177 | 97.1392 | 87.3436
|  | 7869.3868 | 7474.6269 | 7220.0025 | 6983.6955 | 6806.575 | 6621.2183 | 6482.0197 | 6382.6204 | 6284.8667 | 6158.2436 | 6022.6944 | 5850.3599 | 5720.1033 | 5568.4241 | 5404.2868 | 5274.9644 | 5133.5562 | 5005.089 | 4891.6468 | 4521.4388
Reg Up | -191.4184 | -177.257 | -254.2603 | -161.3709 | -254.5451 | -271.3334 | -326.9802 | -232.1386 | -181.6848 | -178.5659 | -210.19 | -258.491 | -224.6203 | -236.9451 | -149.3594 | -163.1072 | -153.0639 | -95.5185 | -69.1902 | -51.0103 | -178.7349
2013
|  | -72.5466 | -159.0671 | 0.72604 | -47.0492 | -113.8043 | -4.9293 | -1.1304 | -34.6473 | -46.7741 | -14.013 | -39.0236 | -24.3739 | -41.6247 | -2.2584 | -36.2682 | 9.8803 | 12.0005 | -7.9751 | -46.2263 | 63.7962 | -5.4227
|  | -116.1771 | 21.8624 | -24.7942 | -10.8017 | -111.3447 | 9.1248 | 14.1685 | -63.7536 | 1.8178 | -57.1356 | -6.2542 | -55.4266 | 24.7109 | 33.5401 | 20.2708 | -30.1921 | 15.6975 | -10.1188 | 4.3633 | -25.14
|  | -104.2172 | 26.1927 | -52.8722 | -57.8937 | 2.492 | -25.0416 | 55.8035 | -74.8382 | -71.3662 | -91.1501 | -28.5089 | -59.8135 | -10.0841 | 35.256 | -16.3384 | 11.1549 | -22.1826 | 15.9922 | -13.3866 | -17.7585
|  | -115.8001 | 39.1872 | -32.1027 | -59.5569 | -27.9859 | 37.9291 | 144.0928 | 30.1864 | -68.4767 | -79.4088 | -21.878 | -27.86 | -6.597 | 11.811 | 2.5257 | 2.4503 | -5.9035 | 31.1402 | 18.6886 | 7.993
|  | -17.3275 | 35.2777 | -53.4209 | -60.1511 | -26.7486 | -34.5057 | 76.5334 | 21.6981 | -92.4315 | -112.8514 | -48.0896 | 4.031 | -22.7242 | 4.9845 | -17.6026 | 24.9372 | 4.4465 | 63.2622 | 34.0986 | -13.8334
|  | -53.6092 | 69.4519 | -18.9975 | -25.2136 | -82.0116 | -10.314 | 61.8656 | 64.5191 | -82.8884 | -103.1906 | -101.154 | 47.1135 | -19.4751 | 17.4097 | 21.0152 | -3.8 | 18.3076 | 86.5314 | 24.7515 | 17.7602
|  | -40.0862 | 68.0217 | 12.6288 | -13.0241 | -115.7188 | -21.1444 | -22.7834 | 49.2967 | -88.0711 | -69.5719 | -105.2653 | 71.5659 | -12.2871 | -6.8579 | -19.2254 | -18.1341 | 44.1133 | 6.4072 | -11.2984 | -20.5717
|  | -104.7642 | -0.97868 | -46.6037 | -22.9366 | -112.3104 | -25.5667 | -6.4122 | 109.2053 | -106.9468 | -71.6872 | -74.9541 | 49.7386 | -26.4344 | -0.75959 | 3.0654 | -32.9332 | 37.6188 | -16.0889 | -0.79099 | 28.5743
|  | -93.0619 | 3.3037 | -54.1676 | 22.4494 | 33.2138 | -45.7996 | 14.1275 | 106.6538 | -127.0534 | -24.7575 | -51.0609 | 50.7461 | -14.4689 | -27.7459 | 30.3857 | -23.1227 | 45.2833 | 10.1458 | -0.78977 | 13.8838
|  | -45.5068 | -36.7234 | 7.7651 | -9.8942 | 95.9182 | -21.3732 | -7.2216 | -24.2723 | 24.9237 | -66.9508 | 17.876 | 45.9242 | -47.1981 | -26.2432 | 29.5203 | -27.4492 | 8.2796 | -26.301 | 3.4843 | 16.3435
|  | -70.1232 | -56.6877 | -20.0705 | -12.0402 | 90.8255 | 21.9296 | 22.4377 | -36.4828 | 73.8415 | -78.016 | -5.7134 | -51.4271 | -42.3671 | -13.8828 | 34.1111 | -45.3613 | -35.3525 | -15.8645 | 23.5692 | 24.5306
|  | -96.4027 | -29.6569 | 6.5865 | -4.1527 | 54.8068 | -18.7474 | 12.2977 | -73.1935 | 104.9353 | -93.8896 | 9.7748 | -76.9958 | -2.3238 | -51.8855 | 32.303 | -27.647 | -52.3247 | -59.2046 | -19.1019 | 9.057
|  | -161.2857 | -12.8257 | 17.1193 | 25.2908 | 78.9048 | -14.3524 | -5.0469 | -60.9881 | 104.5145 | -74.8796 | -148.9914 | -57.9067 | -4.3094 | -47.81 | 25.6968 | 36.9686 | -42.2221 | 63.3416 | -31.4852 | 15.5443
|  | -157.3059 | 41.3229 | -0.37681 | 15.0688 | 13.3781 | -55.3603 | -2.7213 | -30.145 | 109.7585 | -133.2649 | -126.7128 | -88.6646 | 57.3348 | 18.0674 | 0.83182 | 21.1892 | -55.9676 | 111.7198 | 12.1774 | -20.2631
|  | -184.8595 | 69.2468 | 49.8212 | 45.4948 | -49.822 | -22.7428 | -30.0655 | -25.467 | 96.5727 | -40.6588 | -127.3159 | -93.0416 | -12.7781 | -34.0141 | 25.4277 | -27.6991 | -40.9025 | 22.4912 | 22.1958 | 18.5005
|  | -43.5435 | 60.4166 | -28.2082 | -67.5923 | -3.0644 | -77.4016 | -20.8124 | 9.0391 | 59.1061 | 16.5908 | -30.531 | -36.8791 | -15.6893 | 5.0149 | 27.386 | -13.7793 | 27.5345 | -13.3889 | -3.6571 | -20.2682
|  | -42.7402 | 99.8246 | -42.8455 | -81.2342 | 44.4958 | -68.616 | -10.1315 | 39.1354 | 46.4464 | -0.55215 | -37.1489 | -14.3792 | -38.8239 | 8.056 | 9.6515 | -27.4762 | 55.5118 | 32.3586 | 9.3265 | 15.2157
|  | -88.1897 | 91.0975 | -46.6592 | -98.9994 | -91.3699 | -5.0275 | -47.2456 | 81.0196 | 15.6601 | 2.6049 | -46.3675 | -65.5987 | -36.9055 | 14.6397 | -7.4886 | -28.9164 | 29.5453 | 50.2916 | 19.1249 | -16.1215
|  | 3.8157 | 118.8521 | -29.8791 | -73.1371 | -114.2012 | -30.2209 | 8.2982 | 133.3142 | 28.5405 | -59.8256 | -24.6514 | -57.7136 | -37.0338 | 41.5169 | -12.0347 | 97.1243 | 42.7407 | 73.2342 | 14.7149 | -25.8815
|  | -48.0672 | -49.6132 | -46.274 | -91.3918 | 29.6547 | -47.2281 | 17.3288 | 151.6896 | 51.9974 | -18.7741 | -31.4532 | -8.3444 | 116.7994 | 36.1859 | -158.1776 | -3.6805 | -8.6902 | 16.922 | -0.77429 | -2.752
|  | -64.523 | -32.6121 | 22.5281 | -144.3798 | 11.7032 | -71.671 | -15.7804 | -35.5904 | 69.9644 | 26.1457 | 0.93206 | -39.9733 | 106.3344 | 55.278 | -165.4377 | 107.6385 | -8.5602 | 54.1224 | 29.7464 | -4.8771
|  | -29.3175 | -27.1237 | -34.7733 | 5.3933 | 44.3196 | -69.0131 | -32.7676 | -40.2253 | 16.9367 | -85.9752 | -20.8388 | -19.387 | -38.0688 | 55.6056 | -140.4893 | 31.9361 | -25.5335 | 94.7801 | 39.8277 | 0.68846
|  | -65.541 | -13.5694 | -140.3392 | -20.1691 | 104.334 | -67.6724 | -29.6764 | -62.3593 | -11.4837 | -146.6897 | -18.7835 | -18.0319 | 47.5545 | -31.8955 | -18.0429 | -17.2506 | -100.4176 | -19.4345 | 4.3703 | -6.074
|  | -72.1872 | 12.335 | -45.758 | -29.5034 | 62.4889 | 32.4513 | 8.9635 | -61.2051 | -17.4073 | -174.8358 | -30.7108 | -70.123 | 16.6667 | -96.6613 | 20.4357 | -0.6319 | 11.3115 | 23.4927 | 41.3007 | 37.5003
|  | -116.5754 | 10.5915 | -86.4935 | -32.0272 | 148.1473 | -3.4717 | -16.726 | -6.6367 | -12.2345 | -190.2727 | -16.1487 | -91.265 | 12.5699 | -162.4645 | 1.9454 | 21.6801 | 56.2379 | 36.3281 | 34.8257 | 16.7139
|  | 0.098706 | 15.2394 | -129.8629 | -49.0175 | 167.8904 | -13.8517 | 47.7693 | -36.3309 | -45.6389 | -210.422 | -16.5739 | 47.7831 | 28.7087 | 19.2244 | 28.638 | 55.2153 | 28.1263 | 11.3911 | 18.6905 | 28.2072
|  | -5.2708 | -24.8162 | -103.0884 | -64.9866 | 222.7026 | 11.2885 | -58.798 | -36.2407 | -57.1852 | -209.7027 | -43.7909 | 68.7925 | -15.5198 | 5.3457 | -43.0456 | 22.0562 | 91.2531 | 13.9346 | 45.8774 | 42.7932
|  | -19.104 | -8.5618 | -146.1795 | -49.8872 | 261.9594 | 13.0019 | -114.4569 | 25.5384 | -37.6456 | -83.5432 | -83.0517 | -27.6964 | -17.4551 | 15.9129 | -12.9392 | 12.6286 | 4.6634 | 39.4979 | 12.576 | 40.0978
|  | -63.9354 | -71.6099 | 25.4331 | -23.2795 | 275.0051 | 1.818 | 0.68015 | -25.3745 | 52.5639 | -153.0006 | -100.1216 | -26.2869 | -11.3723 | 10.1389 | -39.1649 | -25.4379 | 30.3641 | 1.2162 | 71.7879 | 53.7199
|  | -57.4964 | -73.7505 | 10.9637 | -22.1583 | -1.8228 | 40.3122 | -31.41 | 52.7454 | 81.0662 | -148.92 | -91.2179 | -41.471 | 9.8556 | -5.8422 | -61.0126 | 46.0496 | 29.0014 | -3.3712 | 63.1088 | 80.7903
|  | -47.2206 | -76.1964 | 43.8296 | -49.126 | -23.1662 | 87.9547 | -56.2174 | 19.8002 | 124.0693 | -173.2429 | -125.8077 | -76.6033 | -24.9002 | 48.0608 | -50.5999 | 60.9329 | 42.4682 | 37.0254 | 52.3171 | 88.2089
|  | 11.2821 | -8.2362 | 146.0795 | -10.1446 | 13.5326 | 85.5957 | -50.4627 | 14.3822 | 120.3474 | -34.5352 | -115.6365 | -78.2271 | 107.3675 | 83.741 | -79.4898 | 68.7292 | 46.6768 | -0.6596 | 56.7266 | -66.8766
|  | -3.625 | -33.1752 | 52.798 | -3.7462 | 27.3309 | 140.1728 | -87.4913 | -2.4717 | 124.1629 | -57.4788 | 19.0819 | -67.4819 | -106.1637 | 23.0969 | -74.6168 | -14.8762 | 84.1454 | 35.5529 | 6.8298 | -12.6765
|  | 51.7453 | -38.0598 | -40.0233 | -10.1246 | 29.1554 | 234.8257 | -61.4754 | -56.7384 | 99.1384 | -86.2928 | 26.7451 | 44.2738 | -94.106 | 24.2453 | -100.1699 | -43.8233 | 82.2332 | 63.4526 | 46.7827 | -35.8991
|  | -29.3776 | -50.3747 | -38.5658 | 15.641 | 29.9978 | 261.6903 | -24.2012 | -81.4407 | 28.3403 | -63.2286 | 17.1069 | 56.7224 | -74.4861 | -37.0966 | 87.1265 | -26.6055 | 22.2879 | 79.6044 | 38.8695 | -25.9326
|  | -13.545 | -28.5044 | -29.1914 | 15.0388 | 29.8762 | -19.9313 | -27.7299 | -35.9732 | 54.7675 | -105.1848 | -27.3021 | -67.9633 | 3.5045 | 41.0633 | 79.953 | 61.3127 | 15.3621 | 69.9246 | 26.7439 | -46.0411
|  | 14.8368 | -16.672 | -46.2274 | 36.7826 | 26.3233 | -101.0308 | 11.7802 | 11.951 | 74.3246 | -89.2736 | -34.4786 | -86.2762 | 78.7026 | 35.3323 | 85.6767 | 59.3447 | 22.3573 | 7.0214 | -18.4247 | -16.3958
|  | -32.1681 | -7.5882 | -3.3969 | 60.9905 | -16.5127 | -79.7892 | 8.8727 | -35.1911 | 68.5233 | -109.6109 | -49.4419 | -14.93 | 4.7841 | -46.223 | 18.3174 | 89.3683 | 90.0468 | 13.1469 | -10.3551 | -5.6466
|  | -37.1883 | -33.963 | -20.5266 | -3.2107 | 15.3418 | -79.162 | 1.1703 | -137.6589 | 83.6528 | -103.7489 | -94.595 | -17.2847 | 9.2162 | -10.7681 | 4.6408 | 81.8589 | 67.1115 | 75.1433 | 72.7623 | 24.2358
|  | -84.2132 | -30.5222 | -24.7199 | 23.1994 | -22.2619 | -59.8685 | 30.5062 | -153.6828 | 45.8927 | -104.4015 | -85.023 | -98.43 | 48.3284 | -19.7799 | 15.8592 | -4.8782 | 78.8276 | 21.0368 | 100.1594 | -0.89928
|  | -83.0605 | 17.7942 | -30.9463 | 3.975 | -9.078 | -9.8185 | 52.8915 | -106.1851 | 23.0218 | -102.5506 | -70.6851 | -121.4388 | -43.6979 | -9.8217 | 59.403 | -16.4015 | 23.0086 | -2.9125 | 9.0337 | 25.0617
|  | -73.1986 | 16.0141 | 61.2284 | -16.0003 | -2.6653 | -32.5138 | 86.5572 | 19.9226 | 0.74919 | -43.351 | 61.9807 | -146.8109 | 37.4886 | -0.59411 | 98.7624 | -17.5433 | 13.2137 | 58.9556 | 42.6556 | 16.3366
|  | -75.5283 | 97.0025 | -27.0387 | -10.2471 | -7.9032 | -40.9371 | 123.3287 | 126.7189 | -44.152 | 8.043 | 19.3478 | 23.0497 | 109.0045 | 40.3676 | 85.0992 | 1.96 | -2.2154 | 22.7395 | 24.7119 | 27.1278
|  | 6.3761 | 32.3986 | 11.1884 | -24.2473 | 21.7173 | 105.1277 | 162.8821 | 95.1419 | -92.6156 | -12.5988 | -46.1304 | 71.53 | 164.2116 | 35.5808 | 85.2671 | 0.16474 | 55.5263 | 65.1562 | -15.0391 | 17.3254
|  | 3.5043 | 28.8592 | -9.5294 | -35.5519 | 66.7722 | 126.6219 | 208.6872 | 39.242 | -49.5853 | -23.4468 | -85.9372 | 67.351 | -13.6573 | -34.3384 | 6.6427 | 56.5595 | 60.5935 | 49.7229 | -14.4446 | 30.1741
|  | -3.0597 | -43.3466 | 45.4942 | -42.2801 | 19.3074 | 146.4248 | -106.3075 | -54.9306 | -95.3622 | -92.7524 | -62.562 | -7.7588 | -72.8952 | -76.5378 | 8.8657 | -96.7738 | 88.1226 | 51.4229 | 64.2196 | 27.758
|  | 37.609 | -48.3334 | 90.0315 | -54.8152 | 19.6756 | 165.6685 | 12.7384 | -84.875 | -112.0025 | -39.395 | -119.7146 | 121.9375 | -63.8219 | -81.9877 | -31.7109 | 81.117 | 51.5152 | 42.2364 | 90.7944 | -8.4608
|  | 35.0879 | -50.5047 | -32.7896 | -31.2601 | 23.3238 | 71.1071 | -47.2868 | -13.3685 | 9.8934 | -44.8087 | -98.9949 | -33.6008 | 79.9103 | 53.6902 | -40.5903 | 62.2022 | 69.87 | 50.0328 | 13.8446 | -3.6522
|  | 50.6652 | 12.6973 | 0.83258 | -12.2454 | 47.2014 | 71.5813 | -36.7586 | 77.0581 | -3.6617 | -96.585 | 69.2036 | 26.6987 | 70.2738 | 63.7213 | -57.6034 | 68.5177 | 63.7074 | 39.3277 | 5.2857 | -15.1231
|  | 4.8652 | -7.0212 | -13.5058 | 23.3742 | -44.4128 | -4.7092 | -60.0841 | 23.8023 | -18.7292 | 13.6927 | 124.0274 | 12.317 | -51.961 | 106.336 | 71.4009 | -61.2923 | 25.5125 | 63.2483 | -13.8247 | 12.3642
|  | 17.5625 | -21.0745 | -1.8408 | 56.9852 | 63.6312 | -15.9334 | -72.3034 | -97.0113 | -64.3971 | 39.1818 | -32.3433 | -24.6925 | -97.7173 | -121.8285 | 75.5667 | -55.3184 | 17.8418 | -17.3797 | -14.9653 | 85.5131
|  | 1.2098 | -35.106 | 18.7288 | 69.0749 | 13.94 | -28.1843 | -77.6286 | 12.5827 | -69.3132 | -41.6053 | -62.9627 | 65.1734 | -94.7525 | 107.3444 | 88.6292 | -6.9616 | 32.1083 | -29.5757 | 0.61347 | 67.6831
|  | 11.8142 | -62.0492 | 27.3039 | 16.9515 | 14.6807 | -69.3664 | 24.553 | 14.4556 | -80.5099 | -33.4633 | -80.6652 | 59.6873 | -116.7527 | 130.8938 | 38.7072 | -17.5483 | 68.0894 | -27.404 | -10.6362 | -6.1664
|  | -23.2424 | -22.4944 | -19.0029 | 59.6168 | 129.544 | -97.1709 | 78.9013 | 37.9812 | -95.4312 | -55.419 | -6.7966 | -98.4673 | -145.5432 | -88.2756 | 0.47627 | 5.6893 | 111.6505 | -22.7086 | 16.425 | -12.3328
|  | -13.7137 | -17.4653 | -17.5086 | 84.243 | 110.5453 | -123.9637 | 101.8507 | -92.0568 | 15.4312 | -89.2976 | -33.66 | -65.8341 | -23.955 | -97.1806 | 17.6392 | 44.2567 | 130.7113 | 11.8418 | 13.3383 | -18.4992
|  | 6.69 | -30.7367 | -23.2911 | -29.0757 | 33.2383 | -58.6681 | 180.948 | -99.3088 | 13.2148 | -39.2927 | -72.8068 | -86.2528 | -9.8588 | 27.6289 | -36.2951 | 26.7096 | -29.6786 | 15.0225 | 44.9261 | -24.6656
|  | -13.6435 | -22.7807 | 30.9408 | -91.1797 | -6.9106 | -53.7159 | 215.174 | -90.9749 | -100.0568 | 13.5364 | -58.6578 | -13.0475 | 24.1074 | 36.5028 | -75.7836 | 64.6612 | -44.7104 | 54.7253 | 33.1477 | -30.832
|  | -25.3821 | -46.7481 | 43.1545 | -106.0844 | -110.813 | -44.9122 | 166.175 | -134.7793 | -166.9779 | -96.0365 | -52.3276 | -68.1026 | 25.2583 | -88.779 | 128.2326 | 33.5041 | -56.1867 | -20.5718 | 56.5467 | -9.3145
|  | -42.1424 | -16.4794 | 22.5946 | -108.4751 | 16.5333 | -5.5816 | -67.8213 | -18.2461 | -183.1964 | -7.3955 | -4.6645 | -123.1577 | -50.1866 | -41.1031 | 104.6516 | 65.4006 | 44.2912 | -37.3705 | 11.6711 | -23.6484
|  | 14.7402 | 4.3754 | 61.1467 | -145.3689 | -29.4702 | -46.6982 | -105.6403 | -4.8189 | -51.6351 | -23.5577 | -44.9702 | -23.9445 | -58.7572 | 31.6738 | -35.8645 | 65.2221 | 22.5624 | -4.9534 | 1.6341 | -33.9916
|  | 18.1922 | 12.1281 | 50.0705 | 80.4656 | -134.0111 | -33.3342 | -87.6292 | 37.2666 | -39.1574 | 19.8286 | -88.13 | -47.889 | -66.0291 | 44.7144 | -84.8131 | 74.1597 | 60.1616 | 107.9749 | -38.6528 | -10.8225
|  | 2.5508 | 15.2872 | 47.5973 | 143.1108 | -113.4944 | -23.3628 | -19.1918 | -0.67768 | -35.1597 | -1.0315 | -109.2808 | -71.8336 | -66.7855 | 82.073 | -73.0481 | 69.7077 | -19.2429 | 90.1019 | -38.0697 | 26.1408
|  | 29.2965 | 15.4357 | 18.4239 | 187.9296 | -76.6121 | -48.1023 | -62.3388 | 38.9496 | -53.0969 | -34.8381 | -113.1856 | -95.7781 | 0.56886 | -60.9965 | -94.603 | 75.0871 | -49.7227 | 75.3989 | 46.6945 | -18.4535
|  | 48.7241 | 5.1982 | 48.2458 | 220.2164 | -141.4153 | -0.79732 | 47.3064 | -30.2168 | -61.4062 | -39.0068 | -97.212 | -119.7226 | -12.8074 | -92.5776 | 22.7442 | 11.4284 | -70.1076 | -45.8818 | 37.0332 | -9.2754
|  | 157.7346 | 8.2362 | 64.5294 | 215.0594 | 2.8576 | 13.1017 | 109.4881 | -81.3038 | -97.7466 | -46.582 | 33.2666 | -143.6671 | 10.7421 | 23.4247 | 31.4973 | -30.7144 | -85.2267 | -46.6047 | 42.7754 | -29.5961
|  | 219.049 | 6.8839 | 115.6529 | 222.3225 | -1.2087 | 48.3093 | 65.8757 | -16.0747 | -55.675 | -58.6463 | 14.7609 | 267.9431 | -8.3387 | -24.5249 | -22.6655 | 50.6793 | 11.6854 | -29.1061 | 16.9776 | -15.2878
|  | 180.0621 | -16.3726 | 59.93 | 34.5462 | -18.0868 | 76.6097 | 101.4477 | -17.3415 | 9.1417 | 0.81281 | -22.8328 | 533.2828 | -99.2212 | -10.907 | 19.7454 | 57.1837 | 30.9526 | -6.9272 | 10.3389 | -6.1867
|  | -30.2873 | 31.1022 | -15.7125 | -5.0451 | -3.0294 | 53.3577 | -90.6384 | -10.1623 | -44.1798 | 23.2135 | -53.3939 | -160.5788 | 453.7151 | 34.7138 | -52.3949 | 84.9149 | 51.4316 | 40.0949 | 11.34 | -28.1139
|  | -95.9894 | 20.4587 | -6.9847 | 19.2789 | -12.2916 | 25.4737 | -139.0938 | -15.4179 | -92.5865 | 11.7552 | -91.2749 | 104.4295 | 381.9296 | 69.6725 | 79.6912 | 65.1245 | 7.5974 | 14.0905 | 32.436 | -14.7913
|  | -27.6828 | 8.1764 | 14.4291 | 40.2427 | -6.46 | 114.9074 | -18.8788 | -27.4598 | -44.3056 | -26.3106 | 32.6517 | 110.145 | -85.8248 | 62.9391 | 68.093 | 10.0486 | 69.6948 | 11.3546 | 59.2819 | 56.3381
|  | -43.8489 | 21.8704 | 71.2446 | 14.309 | 8.2305 | 101.2166 | -64.3245 | -82.942 | -55.1527 | -64.6365 | 79.377 | 122.0495 | -121.928 | 67.0371 | 84.0786 | 18.4971 | -11.118 | 31.5132 | 37.1699 | 56.9654
|  | -73.9247 | 60.9757 | 77.62 | -38.2556 | 4.389 | 146.4454 | -38.2975 | -76.3741 | -33.5548 | -93.8702 | -50.2487 | -73.5058 | -132.7315 | 364.4624 | 104.885 | 36.7901 | 38.4823 | -3.761 | 43.3373 | 57.0649
|  | -96.9632 | 52.3553 | 4.609 | 105.455 | -23.7967 | -59.7012 | -66.6252 | -102.3453 | -63.6203 | -149.344 | -103.5247 | -7.3308 | -13.6042 | 329.4383 | -46.1087 | 42.4706 | 24.6016 | 14.4625 | -28.4251 | 41.2979
|  | -114.7009 | 6.0832 | 3.2075 | 48.822 | -66.0621 | -76.9386 | -114.298 | 75.7319 | -55.9489 | 10.5436 | 44.4957 | 46.7677 | -25.8219 | -9.441 | -28.3332 | 84.1217 | 74.1892 | -1.0768 | -10.9552 | 63.0617
|  | -134.3944 | 20.8807 | -9.2585 | 44.0225 | -84.87 | -49.835 | -121.7592 | -20.3969 | 75.8783 | -69.098 | 42.0075 | 76.8211 | -31.5476 | -54.0879 | -24.137 | 16.8735 | 16.0806 | 11.8121 | -26.3523 | 46.5173
|  | -39.7806 | 9.691 | -15.9399 | 86.9486 | -107.369 | -78.1278 | -30.8795 | 24.7892 | 58.2722 | 42.0287 | -19.2176 | -40.4214 | -41.7674 | -37.6163 | -43.0174 | 50.3439 | 13.1723 | 33.0391 | 4.0912 | 19.8904
|  | -34.4196 | 68.8403 | -17.8608 | 113.1707 | -88.2697 | -121.3501 | -73.6971 | 13.7699 | 50.173 | 42.1889 | -56.9753 | -69.8108 | 31.1001 | 30.3301 | -62.9598 | 77.3456 | -16.7964 | -36.3708 | 0.73016 | 9.0297
|  | -28.0822 | 78.3662 | 1.9818 | 64.7681 | -124.7974 | -121.233 | -98.2609 | 18.2125 | -41.443 | 62.8061 | 50.1134 | -121.9211 | -5.1374 | 12.6527 | -3.6551 | 30.6999 | 30.4646 | -23.0727 | 36.6037 | -46.2939
|  | 18.3545 | -65.1106 | 27.07 | 67.9345 | -129.2476 | -48.2053 | -36.6961 | 4.3834 | -34.6899 | -5.5663 | 48.0469 | -6.4339 | -28.7231 | 52.7647 | 28.3278 | 7.7758 | 20.398 | 14.5572 | 36.8226 | -25.9259
|  | 50.8439 | -78.873 | -3.6064 | -45.1204 | -87.9887 | 42.0389 | 129.2124 | 1.3817 | -3.7896 | -19.7667 | -26.4129 | 30.0798 | 60.8718 | 41.9304 | 38.7237 | 44.0339 | 39.0263 | 8.7722 | 49.8749 | -62.5133
|  | 20.2044 | -85.3951 | 0.44141 | -116.2863 | -52.9152 | -29.192 | 167.2811 | -7.1608 | -10.2642 | 8.8281 | -32.1777 | -57.0897 | 89.067 | -15.8762 | -27.3629 | 1.6166 | 80.9344 | 44.7242 | 35.9719 | -95.8177
|  | -30.1219 | -100.2596 | 51.21 | -109.4677 | -28.832 | -5.5852 | -27.4602 | -34.9942 | -18.3437 | -26.7259 | -64.212 | -48.8167 | -39.8943 | 4.3911 | -28.5498 | 32.9801 | 105.8859 | 2.5053 | 16.1621 | -13.5446
|  | -78.3915 | -98.216 | -37.5616 | -96.9174 | -7.6156 | -179.4976 | 6.5381 | -16.883 | -107.2473 | 64.2157 | -48.6164 | -20.6198 | -0.13992 | -21.4966 | -48.2349 | 53.54 | 92.7182 | 21.0158 | 13.7249 | -6.8355
|  | -85.4809 | -18.2282 | -36.304 | -113.7378 | 8.3106 | -156.416 | -21.9194 | -16.1874 | -92.7136 | 65.8808 | 56.8214 | 7.5712 | -29.2298 | 22.8513 | -4.1868 | 50.1436 | -20.3292 | 31.6109 | -26.6294 | 34.2315
|  | -87.3493 | -72.5255 | -21.5035 | -156.8982 | 4.3975 | -107.2925 | -29.7857 | -28.5628 | -77.5638 | -27.8948 | 62.8197 | -25.4242 | -37.7442 | 36.7396 | 16.3938 | 51.894 | -5.6289 | -19.7585 | 21.0966 | 36.9699
|  | 52.5557 | -39.5866 | -35.9519 | -6.7065 | -40.3695 | -104.2416 | -29.6927 | -17.764 | -20.6159 | 27.7405 | -41.1377 | 8.027 | -8.6306 | 30.8115 | 48.6981 | 39.0499 | 2.8045 | 12.4719 | 39.9355 | 30.7923
|  | 114.174 | -56.9667 | -19.1016 | 13.8457 | -84.7378 | -31.9617 | 22.7537 | -61.1193 | 40.496 | 28.5757 | -14.6093 | -20.6872 | 42.3151 | 49.1273 | 24.3064 | 42.3827 | 24.1034 | -24.2727 | 11.0474 | 2.335
|  | -37.8433 | -33.794 | 11.6552 | -4.4761 | -15.4567 | -71.2614 | -29.3467 | -31.6571 | 65.6719 | 39.6645 | 3.3926 | -13.0654 | -6.1286 | 66.9544 | 59.4328 | 42.7598 | 35.5645 | 48.4062 | 1.9461 | -22.2784
|  | -46.0563 | -18.0874 | 4.3089 | -28.6147 | -6.7692 | -66.3212 | -37.7742 | -53.4037 | 52.5087 | 9.7972 | 24.4081 | -1.3977 | 9.5119 | 22.7673 | 76.9912 | 55.3886 | 30.981 | 17.9102 | -6.8751 | -0.3018
|  | -35.3474 | -43.0946 | -3.3727 | -17.4345 | 0.78887 | -96.567 | 180.4637 | 4.6922 | 55.899 | 31.6133 | 48.2969 | -23.5499 | 23.5002 | 8.1293 | 33.9393 | 42.8168 | 22.2417 | 17.5508 | 25.1626 | -13.5743
|  | 2.9953 | -19.4558 | -0.56394 | -13.0965 | 14.2138 | -96.2664 | 132.2762 | -9.3332 | 16.0651 | 22.8341 | 100.1597 | -4.967 | -247.6076 | 36.0832 | -23.6893 | 72.8799 | 31.0402 | 53.8005 | 13.191 | 8.1018
|  | -7.2724 | -63.212 | 28.2205 | 0.30933 | 20.2188 | -103.226 | 94.3092 | -10.1082 | 51.6755 | 55.2192 | -12.5797 | -22.3698 | -214.5455 | 35.0373 | -29.8604 | 85.6944 | 11.9704 | 75.0456 | 43.1099 | -12.2928
|  | -40.741 | -57.451 | 39.1764 | 2.294 | 44.0498 | -77.0641 | 92.6299 | 9.0988 | 32.3286 | 71.0616 | 23.2192 | -31.7674 | 110.1909 | 49.8597 | 52.3776 | 68.0494 | 1.848 | 88.9879 | 30.083 | 18.4085
|  | -32.5645 | -78.0315 | 49.9837 | 4.0551 | 33.3473 | -43.04 | -10.5754 | 9.6816 | 77.4148 | -21.5353 | 31.4203 | -49.6456 | 195.6948 | 4.2045 | 30.6344 | 42.9215 | 5.5098 | 62.0586 | 39.2521 | 6.7259
|  | -11.0224 | -46.3438 | -9.5291 | 4.3268 | 50.1479 | 35.6239 | -31.0269 | -42.3644 | 99.7607 | 18.9477 | -43.4217 | -108.9916 | -13.5019 | -2.8242 | 48.371 | 32.3023 | 30.3645 | 39.0016 | 52.8422 | -5.1451
|  | -37.4862 | -26.9468 | 9.8892 | 2.9632 | -14.4519 | 9.8108 | -31.6225 | -36.8346 | 5.0484 | -48.7694 | 1.5016 | -178.4258 | 42.4979 | 193.8385 | -9.6028 | 4.2962 | 57.0828 | 35.9965 | 0.92248 | 21.6826
|  | -19.8107 | -45.585 | -43.9991 | 41.7585 | -89.2219 | -40.925 | -54.0602 | -57.7697 | 0.46517 | -13.3088 | -48.795 | -232.602 | 4.3223 | 105.9185 | 1.9515 | 12.04 | 80.1711 | 60.9945 | -2.6632 | -1.6459
|  | -27.4718 | -59.3295 | -99.5731 | -31.2325 | -88.646 | -0.85831 | -151.6595 | -37.1102 | 9.0302 | -106.825 | -15.8777 | -207.737 | 15.6907 | 89.8774 | 0.35966 | 37.1437 | -1.8637 | -73.9108 | 8.7499 | 5.8229
|  | 34.2786 | -103.7307 | -114.6892 | -25.7894 | -69.015 | 68.2451 | -51.1151 | -74.6716 | -0.12425 | -141.6507 | 4.5618 | -15.477 | 18.5196 | -80.6742 | 60.1876 | 55.8841 | 3.6563 | 18.8427 | 16.9861 | -4.9054
|  | 3.3568 | -105.6662 | -131.1867 | -11.8448 | -62.4632 | 43.8269 | -84.8986 | -41.3218 | 21.9105 | 134.8903 | -9.1508 | -22.6669 | -47.3418 | -26.2674 | 20.6456 | 27.7117 | 23.45 | 12.928 | 20.6103 | 2.6645
|  | -8.2107 | -92.9891 | -14.5541 | -32.4092 | -10.7199 | 37.9679 | -26.2572 | 2.3703 | 47.8025 | 18.405 | -7.6767 | -21.5527 | -71.0559 | -25.3964 | 31.7891 | 2.9863 | 5.4017 | 39.2143 | 5.7375 | -19.5379
|  | 28.7718 | 24.1021 | -37.9676 | 10.098 | -18.3056 | -36.6687 | -38.4625 | 25.8313 | 53.7114 | -99.8979 | -137.123 | -10.9434 | -42.4032 | -39.7534 | 42.087 | 51.0681 | -15.9618 | 21.714 | 4.5748 | 14.8289
|  | 2.7951 | -16.4325 | -62.1378 | -43.2352 | 32.5796 | -77.9812 | -3.4505 | 1.8643 | -17.9814 | -121.7351 | -115.8844 | 16.9457 | -15.8939 | -21.284 | 60.1417 | 6.6786 | 5.4208 | 15.7719 | 16.2519 | -35.174
|  | -8.9897 | 61.0245 | -70.2619 | -58.3711 | 64.4384 | -83.2922 | -38.2033 | 22.9243 | -16.4924 | -137.9422 | -64.8741 | 122.2394 | 12.2978 | -0.99968 | 60.6241 | 6.0392 | -0.7669 | -1.9795 | 83.2266 | -76.5315
|  | -8.2815 | -3.4923 | -66.7028 | 4.9387 | 103.5673 | -131.144 | 27.7332 | 53.4029 | -39.6114 | 38.5946 | -13.6754 | 70.4256 | 39.6794 | 1.3947 | 29.4464 | -137.2533 | -0.32065 | 29.4176 | 26.5639 | -18.3586
|  | 10.9048 | 17.3957 | 19.9505 | 55.5849 | 168.0196 | -155.9385 | 14.8466 | 74.1945 | -48.7932 | -144.8863 | -23.7438 | 88.749 | -13.5095 | 10.1692 | -29.1297 | -160.5899 | 36.687 | 46.6747 | 49.703 | -44.7734
|  | 12.0452 | 10.2329 | 51.7707 | -35.6608 | -65.1845 | -167.5849 | 9.4017 | -15.2096 | -32.4194 | 28.5782 | 36.9942 | 10.8024 | -10.3722 | -4.8478 | -6.8959 | -136.8659 | 43.5543 | -19.4693 | 49.7222 | -84.318
|  | 20.1202 | 29.6765 | 62.2418 | -60.7402 | -56.917 | -157.5722 | -15.298 | 0.42714 | -25.1985 | 26.2427 | 79.7414 | -21.2023 | -0.92931 | -5.2967 | 3.7739 | -108.7124 | 13.8489 | 2.5423 | 43.5672 | -111.6745
|  | 14.0094 | 9.4833 | 103.4314 | -88.8328 | -68.7254 | -107.0895 | 15.4495 | -10.795 | 31.3105 | 16.6951 | -59.582 | -10.8182 | 118.5641 | 37.6576 | -1.765 | 1.9251 | 19.5818 | 18.3747 | 63.3578 | -118.3869
|  | 64.2743 | 0.189 | 5.8851 | -113.8312 | -44.0371 | -38.2129 | -1.6689 | -46.6791 | -75.2671 | 16.3913 | -46.3839 | -57.7141 | 94.9647 | 131.9876 | -1.4843 | 7.1178 | 4.8593 | 15.0079 | 39.4285 | -207.2646
|  | 75.717 | -16.107 | -14.0246 | -161.56 | -11.5199 | -8.6392 | -35.8991 | -80.3104 | -124.6275 | 22.4661 | -101.5652 | -34.2166 | -9.5555 | 90.7666 | 29.3819 | 24.8422 | 21.7935 | 73.4708 | 43.9034 | 10.797
|  | -44.7957 | -5.3173 | -67.4128 | -188.5778 | 29.4503 | -49.6995 | -30.2711 | -147.8975 | 18.4638 | 53.2912 | -103.4238 | -43.9617 | -63.5272 | 123.4101 | 7.3894 | -8.6022 | 57.8875 | 57.4973 | 19.4064 | 8.536
|  | -32.9122 | -36.3712 | -52.5841 | 109.9822 | 14.3235 | -77.4597 | -46.9571 | 75.2088 | 28.4597 | 147.436 | -65.3324 | -49.1597 | 3.7534 | -40.8056 | 19.433 | 17.9056 | 35.4681 | 26.2101 | 42.8632 | 57.4313
|  | -28.7669 | -15.5102 | -2.0719 | 125.5215 | 14.3311 | -17.7171 | -51.5464 | 51.1154 | 101.129 | -18.6414 | 76.7384 | -77.7288 | -24.6015 | -3.8055 | 31.6961 | 34.2695 | -19.4117 | -5.3145 | -46.5476 | 74.8267
|  | -0.7808 | 2.0931 | 5.4586 | -73.1596 | -32.7295 | 53.5899 | -59.4303 | -34.5014 | 146.9033 | 35.5533 | 74.2891 | 13.6161 | 34.8097 | -20.8123 | -9.222 | 30.3259 | -18.3293 | 2.0945 | -50.3235 | 75.2234
|  | 8.1663 | -45.2216 | 4.4136 | -34.5262 | 38.0432 | 84.4498 | -94.0347 | 71.3933 | 36.9117 | 39.3325 | -49.178 | 75.2425 | 19.338 | -13.2037 | 30.508 | -32.7073 | -14.951 | 7.0721 | -17.5955 | 75.588
|  | -12.3864 | -33.8437 | -83.946 | 34.6301 | -43.5303 | 78.8054 | 14.5156 | -31.6982 | 53.0971 | 28.7796 | -22.2077 | 28.8977 | 72.7078 | -20.7214 | 27.1865 | -47.5759 | -13.1112 | 51.5382 | -11.4871 | 41.6385
|  | 18.7299 | -21.6146 | -75.9744 | 27.4729 | -30.1655 | 117.9067 | -50.77 | -25.0508 | 55.482 | -52.6363 | -12.9809 | 30.9052 | 55.611 | 55.454 | 12.5974 | 34.8112 | 65.3245 | 91.5465 | -13.396 | 17.5757
|  | 57.1325 | -62.8286 | -62.9368 | 11.0617 | -76.7561 | 181.2648 | -74.7412 | -54.2259 | -168.7712 | -24.3617 | 165.5849 | -21.3595 | 31.525 | 21.449 | 27.2884 | 6.5552 | 4.6009 | 65.608 | 14.0064 | 12.5733
|  | 105.0508 | -39.6988 | -67.5697 | -49.2035 | -70.7212 | 7.0155 | -68.1235 | 1.2136 | -152.9266 | -69.777 | 237.8749 | 54.0264 | -12.6379 | 12.0165 | 21.6094 | 42.5447 | 11.1759 | -9.9518 | -2.4634 | -0.21739
|  | 158.9739 | -14.4133 | -80.1641 | -97.3186 | -80.8487 | 44.7082 | -67.8655 | -3.6642 | -9.0012 | 82.2153 | 270.9534 | -47.1241 | 34.1062 | 92.0084 | 19.8756 | 34.3681 | 31.4444 | 39.1721 | -15.6157 | 24.1495
|  | 120.9709 | -52.2174 | -95.6125 | -93.8681 | -87.9275 | 3.4862 | -13.9859 | 58.1762 | -2.6147 | 53.6758 | -13.4633 | -69.6297 | 10.6902 | 99.6374 | 70.352 | 53.8519 | 11.0256 | -34.9486 | 20.9474 | -5.4751
|  | 149.4726 | -69.2777 | -89.8533 | -121.1925 | 5.5518 | -9.2308 | -24.5499 | 17.1219 | 83.4616 | -43.4138 | -15.5667 | -26.1122 | 5.0518 | 45.3836 | -67.0925 | -81.7285 | 56.5279 | 1.9438 | -23.0071 | 11.9808
|  | -20.6544 | 12.7613 | -121.102 | -68.6273 | -31.6333 | 43.6665 | 4.3749 | 61.2704 | 133.6209 | -120.5687 | -9.6744 | 7.5612 | 85.4855 | 64.2716 | -118.9014 | -18.3613 | 28.9335 | -34.8613 | 32.3899 | 35.3755
|  | -68.822 | -17.6656 | -140.8967 | -123.3617 | 9.0708 | 80.0367 | 30.3427 | 90.4388 | 128.0297 | -58.1189 | -4.7541 | -25.6737 | -19.7189 | 30.3903 | 7.6084 | -42.12 | 17.0912 | -46.8038 | 9.7013 | 15.4308
|  | -39.9852 | -3.9898 | -136.0415 | 77.0844 | -29.1498 | 6.1818 | 36.6148 | 31.7765 | 15.6578 | -22.6065 | 16.4147 | 37.3861 | -33.3614 | 23.4067 | 68.9816 | 43.207 | -61.747 | -6.626 | 45.4197 | 42.9835
|  | -112.5859 | -47.2674 | 46.7333 | 97.3199 | -28.8194 | -79.6825 | -34.2134 | -6.6987 | -26.0957 | -4.0001 | -32.9918 | 47.805 | -15.5727 | 38.6529 | -15.7074 | 68.3691 | -70.4576 | -2.4801 | 30.3186 | 23.8855
|  | -103.8779 | -47.2118 | 67.5427 | 1.2565 | -1.1811 | 16.0908 | -23.807 | -3.923 | 2.5639 | -16.0534 | -4.4271 | 42.5155 | -31.2536 | 93.3279 | -17.466 | -9.4505 | -77.0874 | 1.1708 | 51.1595 | 51.3927
|  | -156.782 | -86.9014 | 107.1473 | 13.5514 | -20.4171 | 1.4425 | 90.783 | -12.1648 | -30.6615 | -29.7149 | -143.6235 | 30.7101 | 4.6048 | 48.7407 | -68.1277 | 58.537 | 7.8174 | -38.5225 | -2.9463 | -15.1197
|  | -5.4477 | 8.0335 | 129.1051 | 25.2063 | 1.0548 | -21.9982 | 93.5004 | -8.1051 | 33.2887 | -97.0066 | -157.6901 | 37.263 | 27.448 | 29.772 | 60.9187 | -7.5345 | 17.1269 | -13.4112 | 4.4701 | 17.3875
|  | -9.5209 | -2.2914 | 152.0591 | 3.225 | -29.1851 | -4.8048 | -46.3363 | -15.1738 | -79.6023 | -153.0478 | -166.2741 | -15.6281 | 12.8537 | 65.2492 | 22.984 | -30.2151 | -8.728 | 10.5885 | 32.9675 | 14.4919
|  | -6.5411 | -16.4495 | 162.9904 | 34.9946 | -12.3767 | 20.7072 | -62.8851 | 40.1307 | -71.5442 | -168.1043 | -159.7308 | -31.747 | -24.5153 | -23.6862 | 20.2665 | 3.7523 | 13.0934 | 23.1916 | -3.4036 | 19.5755
|  | -3.3324 | -18.8986 | 117.6642 | 14.2033 | -68.6878 | 33.8978 | -77.3257 | 12.774 | 12.9887 | -161.5201 | 16.4615 | -30.7205 | -31.9219 | 18.8716 | 44.6491 | -3.0335 | 46.3429 | 27.8504 | 29.5492 | 29.2989
|  | 29.6412 | -54.3524 | 29.5425 | -2.0666 | -115.9057 | 68.2556 | 74.9812 | 15.4075 | 55.0779 | -160.7154 | -56.1893 | -2.8937 | 30.8978 | 44.5891 | -1.6281 | 14.9003 | 24.6122 | 62.4996 | -19.8428 | 40.9605
|  | 112.1037 | -19.663 | 69.9639 | -54.2554 | -113.1165 | 91.0879 | -34.7967 | 4.1703 | 86.6131 | 69.7898 | -41.4076 | 76.3187 | -35.5608 | 25.2466 | -9.9259 | -2.2226 | 25.7462 | 19.7902 | -2.9746 | 62.5515
|  | -12.0566 | -41.8125 | 97.9341 | -18.724 | -130.0974 | -55.6218 | -56.4756 | -20.2077 | 106.1169 | 11.223 | 46.6561 | 34.4707 | 5.8513 | -34.8709 | 3.7969 | 26.3014 | 53.553 | 14.4073 | 66.7985 | 46.2587
|  | -34.2168 | -39.5305 | 44.3549 | 28.1869 | -88.063 | -35.3522 | -58.2716 | -70.6926 | 16.1298 | -11.5974 | 33.2748 | 52.727 | 51.4113 | -73.6196 | 19.2427 | -1.995 | 8.9919 | 14.1523 | 60.6491 | -6.2497
|  | -101.0774 | -147.749 | 89.4569 | -16.9464 | -61.372 | -7.8352 | -69.3477 | -59.3633 | 18.2781 | -15.4355 | -18.081 | 56.3578 | 54.8205 | 63.5458 | -5.0153 | 39.5129 | 8.3642 | -27.7307 | 60.522 | 26.3099
|  | -99.9848 | -105.7571 | 90.3293 | 3.3506 | 9.3066 | 14.809 | -72.8888 | -7.2589 | 48.8516 | -6.3234 | -66.0752 | 52.1263 | -6.3591 | 78.8329 | 90.9041 | 22.7804 | -20.6521 | 10.8715 | 76.0049 | 43.9078
|  | -94.5126 | -128.1145 | 115.74 | -7.2888 | -45.2785 | -3.3206 | -69.2231 | -78.8531 | -6.2332 | -30.0707 | -79.259 | 78.4359 | -15.1893 | 69.3444 | 96.8584 | 55.8601 | 27.8069 | 34.2606 | 19.3564 | 73.0882
|  | -89.9564 | -145.3016 | 202.0234 | 6.8251 | -33.9589 | 25.0533 | 0.9773 | -104.7971 | 23.9369 | -7.5577 | -105.5729 | -0.14868 | -10.4427 | -6.9925 | -25.3787 | 26.2509 | 25.4866 | -10.2333 | 60.6453 | 41.1314
|  | 50.0538 | -24.5914 | -24.5716 | 4.4256 | -20.8106 | 43.2348 | -4.8143 | -91.1871 | 16.8032 | -25.4655 | -21.6811 | -60.6544 | 44.4079 | 0.25559 | -24.9671 | 89.8138 | 16.7083 | 20.9805 | -51.3372 | 37.316
|  | 20.6559 | -21.0174 | -22.838 | 31.8041 | -22.7224 | 34.4682 | 18.5802 | -104.4523 | 9.1113 | 28.3535 | -35.8385 | -48.8821 | 15.5261 | 20.9997 | -48.243 | 64.2566 | -8.1462 | 32.6043 | -27.6902 | 32.6315
|  | 32.3184 | -39.9182 | 31.1375 | 26.0124 | -48.0933 | -109.4556 | 53.7305 | -87.6057 | 24.5531 | 100.4693 | -77.6217 | -2.4399 | 29.5803 | -19.2191 | -54.5156 | 44.7075 | 17.5204 | 30.7428 | -10.9172 | 7.9031
|  | 42.9298 | -48.8087 | -23.535 | 10.2751 | -44.867 | -102.4265 | 16.6265 | -23.7223 | 5.9652 | 125.7158 | 22.1536 | 4.4573 | 18.0862 | -25.5929 | -23.402 | 40.6681 | 17.988 | 18.3796 | -44.8003 | -18.8081
|  | 84.9997 | -1.3801 | -35.4396 | 27.4201 | -155.4901 | 38.2143 | 24.6139 | -35.1021 | 14.952 | 107.4799 | 3.4622 | -9.8254 | -45.0745 | 20.0321 | 57.5934 | -22.5381 | 24.6616 | 17.0134 | -41.1747 | 3.9873
|  | 112.463 | -0.074004 | -3.9074 | 59.8903 | -113.7836 | 18.5111 | 44.4408 | -62.8582 | 2.3757 | 115.6141 | -114.1593 | -12.6482 | -78.9236 | 24.9558 | 80.8241 | -45.4354 | -21.915 | 14.9213 | 22.2041 | 24.1741
|  | 40.5327 | 42.1441 | -57.1379 | 45.9493 | -35.3376 | 34.5743 | -85.6635 | 18.3782 | 43.3843 | 96.8159 | -113.4986 | -55.2744 | -29.5116 | 43.7482 | 75.4561 | -49.2382 | 46.3663 | 43.9167 | 14.5581 | -17.3126
|  | 18.3121 | 84.3332 | -10.7085 | 22.4709 | -8.2043 | 18.5839 | -8.5138 | 4.0523 | -95.0684 | -38.7494 | -156.7011 | -64.0023 | 22.2052 | -1.3721 | 59.904 | -18.6988 | 100.9256 | 16.467 | 40.3985 | 37.5247
|  | 3.6825 | 105.5696 | -28.6099 | 31.5482 | 18.1458 | -51.9087 | -24.0496 | -16.3155 | -102.2824 | 32.7595 | -128.1971 | -45.4729 | -40.0332 | 7.3121 | -5.3138 | 10.2304 | -22.0153 | 18.5961 | 17.2523 | 34.6419
|  | 17.9121 | 159.742 | -59.9494 | 19.9153 | 67.5939 | 17.4803 | -55.5595 | 70.724 | -117.2182 | 46.5983 | -61.0232 | -18.5826 | -42.6896 | 69.8764 | 6.6066 | 2.8207 | -1.472 | 23.3761 | 34.7394 | -2.3485
|  | 24.2416 | 193.8155 | -41.9231 | -5.6921 | 31.3717 | -22.274 | -37.9998 | 88.3544 | -7.34 | 75.9231 | 34.3651 | -22.7265 | -12.0877 | 62.5882 | 8.2096 | -26.7709 | 10.4753 | -4.1803 | 40.81 | 13.4531
|  | 16.7365 | -19.9185 | -31.234 | 77.8397 | 71.9511 | -26.6362 | -85.96 | 109.8036 | -0.59895 | 100.1447 | 66.3976 | -76.3553 | -15.1401 | 55.6828 | -10.8482 | -14.4569 | 73.3063 | -10.5215 | 0.74633 | -17.257
|  | 9.4185 | -6.0983 | -5.3714 | 130.8445 | 54.0819 | -24.0119 | -48.2185 | 58.5762 | 8.9259 | -27.1218 | 48.1696 | -87.9488 | 33.7692 | -9.3209 | -23.4116 | 10.9267 | -2.4798 | -12.7375 | -1.5529 | -7.6072
|  | 31.7333 | -82.2614 | -11.5552 | 132.3379 | 84.9363 | -35.723 | -36.9169 | -89.6968 | -21.5082 | -33.132 | 90.3935 | -51.7688 | 59.5657 | -30.3255 | -26.33 | 5.7162 | 31.8815 | 8.8935 | -23.9719 | 13.2484
|  | 14.1764 | -103.8135 | -16.2319 | -38.8167 | 89.0137 | -17.4128 | -53.2467 | -74.4024 | -3.1417 | -30.6485 | 36.0455 | -67.5095 | -8.093 | 83.1408 | 23.1031 | 1.0356 | 56.2119 | 15.9153 | 22.6755 | 35.8896
|  | 11.483 | -146.2819 | -73.6917 | -12.6278 | 84.22 | -8.5759 | -86.7274 | -68.2427 | -2.1045 | -7.4003 | 63.0419 | -50.7104 | -16.806 | 72.0446 | 55.7662 | 7.5332 | 61.7661 | 36.3294 | 30.07 | 33.9986
|  | 18.3457 | -202.865 | -90.7069 | 14.4185 | 104.5681 | 24.3983 | -74.6437 | -97.726 | -15.4881 | -20.6515 | -10.6024 | -9.4708 | 15.1766 | -7.7344 | 76.3662 | 39.6235 | -10.3832 | 47.2075 | 11.0457 | 63.9774
|  | 93.1595 | 24.2864 | -61.746 | 25.8432 | 115.8222 | 41.6467 | -23.8682 | -99.6376 | 8.6636 | 2.2162 | 26.2666 | 10.4492 | 19.1516 | -4.4413 | 93.2504 | 40.78 | -10.4721 | 50.7977 | 46.6315 | 56.7509
|  | -11.681 | -62.2544 | 10.4352 | -11.9347 | -36.8712 | 10.9023 | -80.6493 | -1.7638 | -14.6595 | 111.097 | 53.0555 | -65.1977 | 47.5388 | -5.9586 | -15.2568 | 46.0636 | 5.5331 | 26.9747 | 29.8645 | 79.1877
|  | 10.9193 | -36.7717 | 11.2194 | 27.7692 | 19.6266 | 3.973 | 5.7004 | 0.56705 | 7.441 | 163.0671 | -2.1078 | -35.3395 | 80.9743 | 24.4046 | 35.7302 | 27.9907 | 23.3358 | -8.5131 | 38.1692 | 49.8638
|  | -16.9263 | -82.7396 | -40.5483 | 58.3541 | 33.9799 | 51.9805 | -12.161 | 7.3334 | 24.3513 | 128.0473 | -5.1665 | -32.5774 | 93.9116 | 28.118 | 13.3847 | 42.1197 | -3.1752 | -9.1205 | 5.9465 | 14.21
|  | 18.2804 | -88.721 | 13.1437 | 72.6466 | 56.2969 | 41.6345 | 6.439 | -26.9304 | 5.3869 | -17.5528 | 52.2693 | -26.587 | 19.6003 | 29.5122 | 73.6881 | 50.0019 | 24.7318 | 27.5974 | 29.8581 | 18.2432
|  | 64.7008 | -98.3681 | -25.3121 | 118.2707 | -28.7138 | -13.6042 | -26.6818 | -2.2907 | -14.479 | 14.9969 | 25.7827 | -20.037 | -1.7303 | -12.0247 | -11.0464 | 45.4268 | 3.8961 | 61.5662 | 22.0348 | 22.0748
|  | 35.128 | -89.9041 | 0.8039 | 213.1749 | -22.8374 | -11.0067 | -94.1945 | -15.4588 | -69.416 | 70.8719 | 26.4173 | -3.7342 | 13.0151 | 23.6439 | 44.4484 | 22.1519 | 47.6913 | 73.6625 | 28.4674 | 34.5732
|  | 43.5776 | -67.3573 | -17.4892 | 27.8074 | 36.8555 | 43.9716 | -44.8353 | -53.6162 | -14.9249 | 40.286 | -17.4331 | -7.1731 | 42.1848 | 18.0966 | -32.0226 | 38.0934 | 75.4489 | 81.1094 | 19.625 | -42.9688
|  | 35.3403 | -90.9029 | 39.2609 | 125.5291 | -5.0403 | -37.6599 | -75.8682 | -58.3226 | 16.8069 | -17.8834 | -112.8257 | -18.5952 | 26.5343 | 9.6351 | -14.7707 | 35.895 | 33.709 | 71.2312 | 21.7326 | -7.6001
|  | 64.228 | 13.8587 | 66.4648 | 130.967 | 16.7818 | 0.15711 | -58.0396 | -77.009 | 56.3039 | -18.1307 | -140.7138 | 1.0613 | -2.6515 | 52.7444 | -33.0756 | -44.8122 | 8.0598 | -12.3688 | 5.4115 | -19.653
|  | 140.9928 | -3.3494 | 28.3219 | 152.5914 | 7.7868 | 1.1564 | -48.0604 | -80.2201 | 10.1032 | -54.1614 | -102.3582 | 2.3155 | -13.7525 | -0.5587 | -33.2571 | -51.2827 | 6.1006 | 7.3008 | -19.9845 | 51.4654
|  | 139.08 | 13.3152 | 56.9476 | 99.5264 | -4.0922 | 25.0098 | -42.5293 | -62.1026 | -17.4762 | 60.1952 | -129.3208 | 37.0365 | -21.1369 | 24.1518 | 42.1232 | -45.461 | 0.98428 | -8.5436 | -23.7871 | 56.1037
|  | -31.8568 | -19.0328 | -17.1996 | -60.1906 | -2.5104 | -30.9274 | -88.6246 | -24.4561 | 25.0692 | 95.757 | 9.6433 | 26.3651 | -40.5548 | 10.6153 | 6.278 | 13.1435 | 29.1022 | -13.4921 | -26.2913 | 10.619
|  | 2.6865 | -39.5314 | -4.9947 | -65.6135 | -10.1601 | -52.2863 | -94.674 | -14.4982 | -6.5814 | 112.1197 | -0.5604 | -44.0487 | 21.787 | -8.5315 | 19.0682 | 5.8072 | 2.7874 | -1.7974 | 12.8933 | 56.2097
|  | 5.9065 | -67.7497 | -33.8971 | -64.2017 | -10.6953 | -50.0658 | -0.0050858 | -35.737 | -42.0264 | 59.5594 | 4.7552 | -27.8545 | 38.8601 | -14.4437 | -53.534 | -3.7224 | 16.6077 | 0.52328 | -12.8471 | -49.35
|  | -5.6437 | -85.9027 | -45.6616 | -85.1779 | -15.5434 | -36.4887 | -1.149 | -3.1156 | -46.4899 | 3.5153 | 19.8557 | -28.5346 | 63.6414 | 26.4967 | -27.1008 | 31.8837 | 27.8584 | 6.9352 | 12.1398 | 16.7894
|  | 3.9991 | -148.8617 | -57.2735 | -96.3127 | -7.0366 | -20.1405 | -32.1928 | -32.5364 | -5.4692 | -79.7021 | 4.3406 | -40.0157 | 84.1974 | 40.6099 | -69.8701 | -10.9841 | 29.5452 | -14.2617 | -13.4194 | 10.1853
|  | -23.6357 | -238.3124 | -27.6957 | -91.1598 | -8.422 | 150.5366 | -52.6656 | -24.4686 | -27.0453 | 8.0595 | -8.1276 | -73.4484 | -80.9638 | 101.8029 | 20.1852 | 18.381 | 78.2747 | 5.6976 | 25.1931 | 5.6731
|  | -3.1118 | -261.8517 | -66.2196 | 79.3353 | -8.1592 | 4.7712 | -12.2888 | 5.1523 | -20.489 | -96.2742 | -219.2263 | -69.2005 | 49.5252 | 189.8238 | 5.2743 | 10.4528 | 26.3635 | 48.1495 | 27.151 | -3.326
|  | -14.331 | 32.2906 | -51.8047 | 8.4632 | 16.6268 | 6.0899 | 21.2858 | -31.8675 | 1.257 | -87.9333 | -245.974 | -22.5047 | 45.5137 | -12.601 | 43.2166 | 12.9252 | -5.5257 | 37.7101 | -1.8626 | 17.647
|  | 11.3094 | 9.1473 | -83.7827 | -49.3704 | 22.6492 | -16.4276 | -6.6663 | 50.5691 | -10.4355 | -86.7117 | -264.4493 | -27.4687 | 66.9037 | -17.1595 | -2.7117 | -16.6184 | 21.7762 | 36.8357 | 11.1159 | 18.6931
|  | 9.2399 | -90.0325 | -41.4777 | 39.0025 | 21.671 | -3.283 | -32.4852 | 42.8513 | 39.4455 | -114.5712 | -241.669 | -15.5777 | 63.3851 | -30.5845 | 1.5578 | -3.0083 | 52.4973 | 17.5081 | 3.0204 | 7.0281
|  | 9.3913 | -142.4988 | 4.4863 | 12.3592 | 46.2573 | -32.5607 | 4.4054 | 9.7923 | 79.2497 | -122.913 | -205.2156 | -31.5418 | 82.5022 | -63.5248 | 57.7816 | 8.476 | -5.3809 | -15.2495 | -0.48976 | 28.6223
|  | -8.9608 | -64.3973 | -26.5839 | 59.9996 | 71.763 | 13.0553 | 0.027136 | 0.97049 | 98.8399 | -147.619 | -25.6783 | -60.3492 | 104.6395 | -34.4579 | -26.8528 | 6.3812 | 21.8314 | 46.7416 | -15.1188 | -38.6655
|  | 1.269 | -64.4028 | -58.5319 | 40.6545 | 124.1934 | -101.3264 | -1.8637 | -21.9464 | -34.6972 | -48.3037 | -31.0187 | 26.0469 | -5.3874 | -35.697 | -52.8578 | 36.7171 | -1.2395 | 18.4111 | -48.9103 | -23.1674
|  | -31.3591 | 13.3234 | -76.9564 | -69.9792 | 34.0954 | -175.863 | -6.2546 | -19.311 | -41.9173 | -40.8117 | -58.6321 | 56.1282 | 8.0874 | 6.5133 | -42.8019 | -23.8758 | -16.5897 | -2.2559 | 9.786 | -52.1915
|  | -30.7928 | 31.0862 | -109.4577 | -83.4194 | 28.3384 | -341.1322 | -0.89723 | -27.7632 | -44.9631 | -94.8734 | -66.1442 | -29.5708 | 52.631 | 12.1095 | 56.8548 | -28.5951 | 24.5279 | 13.5863 | -15.5356 | -18.583
|  | 36.4788 | -141.9054 | -126.2043 | -96.0115 | 6.5054 | -297.045 | 41.5275 | -29.8981 | -24.3773 | -11.093 | -96.686 | -19.3749 | 84.808 | 75.2034 | 41.9008 | -14.3623 | 52.8599 | 5.9401 | 22.5571 | -0.020666
|  | -44.9152 | -19.591 | 4.7967 | -208.0144 | -42.0016 | -250.5877 | 55.3056 | -23.6839 | -3.652 | -49.3117 | -177.2056 | 116.8961 | 90.3141 | 39.636 | 53.5685 | 26.89 | 12.1253 | 14.1618 | -2.6997 | 7.7728
|  | -56.4216 | -5.1642 | 70.4336 | -276.6944 | -39.5058 | 10.1348 | -97.8962 | -25.2726 | 5.5829 | 7.2074 | -49.0189 | -29.5368 | 55.5962 | -16.8382 | 65.2672 | 40.6659 | 16.8024 | 11.6357 | 45.7973 | 13.8719
|  | -62.0157 | -61.3987 | 83.7728 | -30.4065 | 5.0771 | 2.5526 | 2.5538 | -24.5768 | -4.3411 | -12.485 | -60.6954 | -42.2752 | 10.815 | 16.0867 | 58.3302 | 30.7622 | 35.373 | 10.4419 | -3.2618 | 54.6321
|  | -51.6318 | -101.2324 | 5.2867 | -4.3239 | 178.6983 | 44.1848 | -254.5405 | -22.1851 | -1.8871 | -24.8228 | 6.7716 | -86.4114 | 14.7815 | -6.3051 | 45.1885 | 14.7073 | 51.8921 | 23.9107 | -3.3166 | 79.5173
|  | -54.0133 | -102.7145 | -15.3887 | 22.5143 | -43.1757 | -46.3367 | 18.3471 | -33.9069 | 22.482 | 6.5826 | -1.3603 | -5.6752 | 37.1622 | 31.3199 | 9.873 | 8.9779 | 57.4866 | -0.98634 | 1.8402 | 82.0046
|  | -8.5269 | -122.1063 | -15.3517 | 1.2999 | -65.025 | -114.5567 | 3.6549 | -0.26523 | -49.2265 | 47.0648 | 59.9595 | 11.9444 | 66.9795 | 12.0859 | 2.9792 | -2.1341 | -22.4161 | 6.0651 | 14.6403 | 79.6439
|  | -18.0974 | 132.6448 | -33.7877 | -61.3542 | -98.4998 | -128.5408 | -31.2427 | -23.6558 | -65.7379 | -26.6627 | 35.6547 | 48.7936 | 67.3887 | -4.7487 | -17.1339 | 35.7582 | -5.4422 | 13.3395 | -10.892 | 42.0707
|  | -9.7419 | 8.5978 | -87.1165 | 26.9807 | -101.6175 | 7.2961 | -43.3391 | -4.3095 | -85.3973 | -47.0989 | -40.4272 | 50.1596 | 83.4033 | 50.7753 | 21.2104 | 29.1676 | -11.3226 | 2.6801 | -2.3023 | 25.5319
|  | 33.6268 | -22.3968 | -168.5527 | 2.3568 | -85.9466 | -49.2782 | 75.7793 | -4.0814 | 2.3118 | -64.5928 | -19.8781 | 131.8946 | -33.3992 | 66.7875 | 14.4209 | 27.6611 | -10.2062 | 12.1348 | 17.5097 | 14.3374
|  | 33.4274 | -82.0235 | 87.025 | 32.6622 | -69.7416 | -38.6485 | 119.1957 | 24.6564 | -22.7595 | 10.6751 | 66.3753 | 2.4 | 43.2649 | 68.884 | -17.7125 | 6.8898 | 21.1262 | -9.6215 | -33.6592 | -2.7166
|  | 14.5699 | -93.778 | 74.2195 | -31.6613 | 50.3216 | -69.8721 | 50.748 | -38.3271 | -44.4665 | 50.3815 | 103.603 | 12.559 | 23.6382 | 75.1231 | 43.0347 | 80.9736 | -8.2114 | -34.1014 | -18.4595 | 0.72304
|  | 25.1093 | -109.7109 | 111.5158 | -33.3721 | 67.2486 | 36.711 | 73.9513 | -38.4801 | -69.0772 | -10.6411 | 87.6789 | 4.6671 | 38.9081 | 110.6657 | 29.8386 | 64.7398 | -16.6163 | -13.2119 | -22.4791 | -26.6402
|  | 3.5825 | -52.1096 | 74.9668 | -31.103 | -105.1078 | 6.3072 | 95.76 | -57.8212 | -87.1391 | 4.9552 | -67.9724 | 34.8071 | 52.7419 | 15.3089 | 84.6974 | 64.7312 | -1.7844 | 6.8041 | 7.1648 | 6.9294
|  | -9.4014 | 9.6497 | -32.4227 | -98.8826 | -160.0506 | 39.9672 | -22.5499 | -73.3938 | -147.0224 | 37.1004 | -92.546 | 39.8781 | 93.2097 | 13.617 | 115.5136 | 11.4492 | -10.201 | 16.9815 | -30.8083 | 10.4468
|  | -2.1278 | 17.572 | -45.1404 | -127.0834 | -161.4774 | -105.833 | -74.4837 | 60.3462 | 19.419 | 63.1553 | -114.5102 | 17.3886 | 90.0615 | 29.0084 | 43.7242 | -2.9649 | -22.7287 | 42.4005 | 37.027 | -21.7338
|  | -32.0676 | -32.989 | -132.2576 | -91.4493 | 31.4533 | -148.8498 | 44.56 | 52.3114 | -21.0923 | 80.1512 | 90.2118 | 66.0409 | 150.7331 | 25.8656 | 16.7137 | -2.0144 | -24.2685 | 13.7171 | 34.7133 | -22.192
|  | -41.38 | -94.6383 | -87.7488 | 11.0357 | 36.8081 | -179.7016 | 69.4229 | -97.2482 | -34.9377 | -90.4909 | -5.2504 | 60.016 | 7.0861 | 89.9908 | 31.7214 | 1.1802 | -6.8489 | 22.6555 | 35.7898 | -24.647
|  | 106.7807 | -111.8742 | -144.5931 | 64.4136 | 97.8224 | -198.9199 | 64.1721 | 89.5934 | -75.182 | -99.5596 | -43.4035 | 80.8741 | 12.7039 | -2.434 | 28.7884 | -22.8052 | 11.6798 | 15.3795 | 65.4338 | -17.9988
|  | -20.3131 | -101.2812 | 83.9525 | -20.9463 | 142.4917 | 97.6462 | -24.2355 | 134.9445 | -32.0073 | 18.9534 | -46.878 | 83.8691 | -47.0974 | -37.9611 | 28.7318 | 13.5525 | -0.036439 | 6.3576 | 66.0569 | -7.3206
|  | -7.8216 | -96.5764 | 122.2949 | -25.6639 | 118.3271 | 14.67 | -56.5597 | -134.6478 | 90.6323 | 57.0805 | -69.3753 | -45.4476 | 3.6438 | -34.2384 | 15.7044 | 0.83879 | 24.7403 | 10.8196 | 86.819 | -26.2953
|  | -76.5636 | -72.4951 | 95.7314 | -82.7121 | 18.8388 | -153.582 | -67.4061 | -157.2639 | -74.8682 | 47.1742 | 57.3557 | -90.1 | 24.0114 | -20.0819 | -9.2129 | 11.3952 | 47.5576 | 31.6191 | 75.587 | -30.6543
|  | -123.4471 | -28.3234 | 20.7912 | -73.1638 | 61.6346 | -195.2654 | 21.2966 | -193.3096 | -131.8588 | -47.8284 | 72.5141 | 22.1134 | 60.8692 | 11.3771 | 197.7087 | 49.0456 | 13.4977 | 31.9208 | -5.6137 | -19.5235
|  | -85.7273 | -17.5036 | -14.1483 | -124.3113 | 37.2995 | -228.0408 | 32.978 | 170.1073 | -133.3579 | -118.5956 | 62.036 | 23.1845 | 60.9301 | 47.8993 | 246.1568 | 47.735 | 16.9471 | -2.1055 | 14.154 | -28.8963
|  | -76.75 | -37.3818 | -3.8002 | -137.3014 | 24.9718 | 2.9855 | 25.7255 | 105.5751 | -140.5713 | -147.8972 | -43.4239 | 51.2985 | 46.7565 | 22.8818 | 30.8059 | 19.0636 | 25.4146 | 18.6229 | 65.8233 | -13.9719
|  | 68.9528 | -52.8942 | -26.3314 | 105.8217 | -47.2946 | 48.3532 | -20.0537 | 113.6578 | -164.4219 | 21.1664 | -54.8912 | 59.8854 | 36.8194 | 47.8559 | 40.8728 | 50.6047 | 35.7781 | 21.2163 | -2.8623 | -13.4045
|  | 102.6841 | -39.1293 | 32.2171 | 125.7455 | -157.6168 | 38.6431 | -59.0774 | 35.1665 | 39.3211 | 29.3343 | 33.7245 | 68.1537 | 24.4561 | 46.5551 | 47.1348 | 92.6678 | 3.8795 | 28.1097 | -4.1288 | -0.17985
|  | 192.3314 | -52.7206 | -41.271 | 7.6165 | -249.1798 | -143.3558 | -145.6486 | 30.3241 | 86.2993 | 27.9115 | 79.0587 | 29.826 | 74.2245 | 61.3461 | -6.5901 | 44.9498 | 16.0803 | 38.078 | 15.263 | 4.7444
|  | 191.1559 | -21.6595 | -16.4923 | -14.8396 | -281.8788 | 115.43 | -185.0773 | -32.375 | -92.0822 | -23.998 | 96.7102 | -104.2972 | 37.2892 | 18.3008 | 31.9754 | 5.7556 | 10.1786 | 37.2752 | 17.6048 | 61.9012
|  | 270.1826 | 21.2708 | -31.9753 | 42.5418 | 93.1221 | 138.9727 | 1.3499 | 42.151 | 81.0273 | -79.6284 | -22.6641 | -134.872 | -18.5479 | 51.336 | 1.5776 | -19.5957 | 40.2747 | 7.5706 | 20.646 | 54.591
|  | 241.9693 | -18.9368 |  | 63.5426 | 108.9634 |  | 38.7824 | 69.0714 |  | -106.2333 | 3.5734 |  | -45.1223 | -10.8565 |  | -11.5411 | 13.781 |  | -6.2248
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| Mean | -6.1918 | -27.0237 | -6.6029 | -5.3053 | -5.6247 | -18.1904 | -10.6984 | -12.4559 | -7.9576 | -25.4431 | -27.9688 | -11.3931 | 9.4724 | 19.6731 | 12.0647 | 16.2316 | 18.6314 | 18.8917 | 15.8625 | 7.4689
| Max | 270.1826 | 193.8155 | 202.0234 | 222.3225 | 275.0051 | 261.6903 | 215.174 | 170.1073 | 146.9033 | 163.0671 | 270.9534 | 533.2828 | 453.7151 | 364.4624 | 246.1568 | 107.6385 | 130.7113 | 111.7198 | 100.1594
| Min | -184.8595 | -261.8517 | -168.5527 | -276.6944 | -281.8788 | -341.1322 | -254.5405 | -193.3096 | -183.1964 | -210.422 | -264.4493 | -232.602 | -247.6076 | -162.4645 | -165.4377 | -160.5899 | -100.4176 | -73.9108 | -51.3372
[18 empty] | 370 | Bin | Frequency
[18 empty] | 360 | -170 | 0
[18 empty] | 350 | -160 | 1
[18 empty] | 340 | -150 | 0
[18 empty] | 330 | -140 | 0
[18 empty] | 320 | -130 | 0
[18 empty] | 310 | -120 | 1
[18 empty] | 300 | -110 | 0
[18 empty] | 290 | -100 | 0
[18 empty] | 280 | -90 | 3
[18 empty] | 270 | -80 | 4
[18 empty] | 260 | -70 | 2
[18 empty] | 250 | -60 | 2
[18 empty] | 240 | -50 | 2
[18 empty] | 230 | -40 | 4
[18 empty] | 220 | -30 | 13
[18 empty] | 210 | -20 | 12
[18 empty] | 200 | -10 | 13
[18 empty] | 190 | 0 | 23
[18 empty] | 180 | 10 | 12
[18 empty] | 170 | 20 | 20
[18 empty] | 160 | 30 | 22
[18 empty] | 150 | 40 | 18
[18 empty] | 140 | 50 | 16
[18 empty] | 130 | 60 | 9
[18 empty] | 120 | 70 | 14
[18 empty] | 110 | 80 | 4
[18 empty] | 100 | 90 | 5
[18 empty] | 90 | 100 | 4
[18 empty] | 80 | 110 | 4
[18 empty] | 70 | 120 | 1
[18 empty] | 60 | 130 | 1
[18 empty] | 50 | 140 | 2
[18 empty] | 40 | 150 | 0
[18 empty] | 30 | 160 | 0
[18 empty] | 20 | 170 | 0
[18 empty] | 10 | 180 | 0
[18 empty] | 0 | 190 | 1
[18 empty] | -10 | 200 | 1
[18 empty] | -20 | 210 | 0
[18 empty] | -30 | 220 | 0
[18 empty] | -40 | 230 | 0
[18 empty] | -50 | 240 | 0
[18 empty] | -60 | 250 | 0
[18 empty] | -70 | 260 | 0
[18 empty] | -80 | 270 | 0
[18 empty] | -90 | 280 | 0
[18 empty] | -100 | 290 | 0
[18 empty] | -110 | 300 | 0
[18 empty] | -120 | 310 | 0
[18 empty] | -130 | 320 | 0
[18 empty] | -140 | 330 | 1
[18 empty] | -150 | 340 | 0
[18 empty] | -160 | 350 | 0
[18 empty] | -170 | 360 | 0
[19 empty] | 370 | 1
[19 empty] | More | 0

## Table H.8 & H.9Reference Tables
[7 empty] | Source: | \Data\Load Following\2014 Study Load Following 06-JUN.xlsm
\Data\Load Regulating\2014 Study Load Regulation 06-JUN.xlsm
\Data\Wind Following\2014 Study Wind Following 06-JUN.xlsm
\Data\Wind Regulating\2014 Study Wind Regulation 06-JUN.xlsm
Table H.8 - Sample Reference Table for East Load and Wind Following Component
Reserves (MW)
Bin | Up | Load | Down | Up | Wind | Down
| Reserve (MW) | Forecast (MW) | Reserve (MW) | Reserve (MW) | Forecast (MW) | Reserve (MW)
| 265.8233 | 10000 | 283.0849 | 358.2738 | 5000 | 157.1056
1 | 265.8233 | 7841.078 | 283.0849 | 358.2738 | 1061.0109 | 157.1056
2 | 250.3262 | 7528.2013 | 192.1411 | 347.6021 | 939.5101 | 212.6743
3 | 199.7954 | 7220.3728 | 285.3671 | 512.3401 | 839.4726 | 205.0938
4 | 315.1626 | 7005.1953 | 293.8452 | 298.4279 | 754.7668 | 290.3599
5 | 262.0571 | 6803.7313 | 334.1146 | 356.3045 | 697.848 | 206.8363
6 | 150.4086 | 6625.9345 | 321.3594 | 197.8167 | 627.4128 | 230.7686
7 | 280.4555 | 6505.9873 | 259.7512 | 239.1613 | 570.7471 | 375.3883
8 | 191.4285 | 6381.0305 | 212.1642 | 332.355 | 501.9783 | 308.2493
9 | 146.8943 | 6265.4996 | 135.308 | 238.074 | 438.4383 | 284.261
10 | 272.5367 | 6167.5107 | 98.5366 | 194.8347 | 395.2009 | 373.6393
11 | 237.0292 | 6016.7172 | 167.5527 | 163.4774 | 354.908 | 171.7324
12 | 198.9593 | 5858.6105 | 338.0864 | 166.4841 | 302.4003 | 240.5495
13 | 278.7293 | 5718.61 | 295.4263 | 115.2678 | 261.5822 | 264.4904
14 | 123.7826 | 5574.4699 | 150.7777 | 113.591 | 225.6494 | 203.0971
15 | 87.1893 | 5406.4174 | 194.7029 | 100.5808 | 196.8741 | 287.0049
16 | 143.5713 | 5264.324 | 171.4752 | 84.2145 | 163.0923 | 325.5284
17 | 178.9486 | 5124.6211 | 97.6629 | 90.4537 | 122.3368 | 225.0038
18 | 102.3869 | 4990.7271 | 85.7778 | 43.7859 | 78.3969 | 242.0931
19 | 87.067 | 4870.2157 | 73.4521 | 34.7156 | 47.0819 | 288.0155
20 | 290.445 | 4505.016 | 63.3152 | 41.2201 | -6.9234 | 81.2795
| 290.445 | 0 | 63.3152 | 41.2201 | -6.9234 | 81.2795
Table H.9 - Sample Reference Table for East Load and Wind Regulating Component
Reserves (MW)
Bin | Up | Load | Down | Up | Wind | Down
| Reserve (MW) | Forecast (MW) | Reserve (MW) | Reserve (MW) | Forecast (MW) | Reserve (MW)
| 177.257 | 10000 | 261.0838 | 373.3669 | 10000 | 172.9845
1 | 177.257 | 7869.3868 | 261.0838 | 373.3669 | 1070.4018 | 172.9845
2 | 254.2603 | 7474.6269 | 182.8268 | 459.2711 | 935.3237 | 228.345
3 | 161.3709 | 7220.0025 | 189.4938 | 297.0996 | 826.968 | 203.0872
4 | 254.5451 | 6983.6955 | 221.6433 | 277.3932 | 761.8554 | 306.293
5 | 271.3334 | 6806.575 | 270.7979 | 392.5417 | 695.3773 | 277.0229
6 | 326.9802 | 6621.2183 | 253.0667 | 233.2848 | 627.5993 | 218.9924
7 | 232.1386 | 6482.0197 | 213.082 | 304.8012 | 561.7415 | 371.7873
8 | 181.6848 | 6382.6204 | 164.1676 | 278.9047 | 508.2169 | 224.9171
9 | 178.5659 | 6284.8667 | 142.6396 | 177.1396 | 439.9878 | 232.5766
10 | 210.19 | 6158.2436 | 158.0261 | 171.5824 | 394.2753 | 406.3662
11 | 258.491 | 6022.6944 | 260.2856 | 130.5454 | 351.4062 | 145.3989
12 | 224.6203 | 5850.3599 | 448.1087 | 134.0238 | 304.706 | 167.9849
13 | 236.9451 | 5720.1033 | 430.5643 | 144.4182 | 263.9233 | 223.5228
14 | 149.3594 | 5568.4241 | 353.1672 | 111.9532 | 228.6697 | 158.3954
15 | 163.1072 | 5404.2868 | 230.605 | 84.5226 | 196.2769 | 278.5089
16 | 153.0639 | 5274.9644 | 104.2477 | 73.8706 | 161.8294 | 494.2333
17 | 95.5185 | 5133.5562 | 124.5642 | 75.6052 | 116.1281 | 239.804
18 | 69.1902 | 5005.089 | 110.5177 | 44.0372 | 82.4322 | 93.5114
19 | 51.0103 | 4891.6468 | 97.1392 | 38.488 | 46.0036 | 153.5153
20 | 178.7349 | 4521.4388 | 87.3436 | 20.7167 | -7.2568 | 112.4515
| 178.7349 | 0 | 87.3436 | 20.7167 | -7.2568 | 112.4515

## Table H.10, H.11 Backcast
Source: | \Data\Exceedence Files\2014 Wind Integration Study - 2013 Exceedance_All Months_Final.xlsx
Table H.10 - Load Forecats and Compnent Reserve Requirement Data for Hour- ending | [8 empty] | Table H.11 - Interval Wind Forecats and Component Reserve Requirement Data for Hour- ending
11:00 a.m. June 1, 2013 in PACE | [8 empty] | 11:00 a.m. June 1, 2013 in PACE
East | [8 empty] | East
Time | Actual Load (10-min Avg) | Actual Load (Hourly Avg) | Following Forecast Load: | Load Following Up Reserves Specified by Tolerance Level | Load Following Down Reserves Specified by Tolerance Level | Regulating Load Forecast: | Load Regulating Up Reserves Specified by Tolerance Level: | Load Regulating Down Reserves Specified by Tolerance Level: | Time | Actual Wind (10-min Avg) | Actual Wind (Hourly Avg) | Following Forecast Wind: | Wind Follow Up Reserves Specified by Tolerance Level | Wind Follow Down Reserves Specified by Tolerance Level | East Wind Regulating Forecast: | Wind Regulating Up Reserves Specified by Tolerance Level: | Wind Regulating Down Reserves Specified by Tolerance Level:
2013-06-01 10:00 | 5337.3203 | 5395.1377 | 5343.6814 | 143.5713 | 171.4752 | 5319.1862 | 153.0639 | 104.2477 | 2013-06-01 10:00 | 190.2152 | 216.9613 | 206.6451 | 100.5808 | 287.0049 | 218.6705 | 84.5226 | 278.5089
2013-06-01 10:10 | 5382.9462 | 5395.1377 | 5343.6814 | 143.5713 | 171.4752 | 5350.0131 | 153.0639 | 104.2477 | 2013-06-01 10:10 | 208.492 | 216.9613 | 206.6451 | 100.5808 | 287.0049 | 192.6782 | 73.8706 | 494.2333
2013-06-01 10:20 | 5385.8284 | 5395.1377 | 5343.6814 | 143.5713 | 171.4752 | 5362.7058 | 153.0639 | 104.2477 | 2013-06-01 10:20 | 212.3819 | 216.9613 | 206.6451 | 100.5808 | 287.0049 | 195.1411 | 73.8706 | 494.2333
2013-06-01 10:30 | 5402.8477 | 5395.1377 | 5343.6814 | 143.5713 | 171.4752 | 5375.3985 | 153.0639 | 104.2477 | 2013-06-01 10:30 | 230.6569 | 216.9613 | 206.6451 | 100.5808 | 287.0049 | 197.6041 | 84.5226 | 278.5089
2013-06-01 10:40 | 5433.4525 | 5395.1377 | 5343.6814 | 143.5713 | 171.4752 | 5388.0912 | 153.0639 | 104.2477 | 2013-06-01 10:40 | 233.9398 | 216.9613 | 206.6451 | 100.5808 | 287.0049 | 200.0671 | 84.5226 | 278.5089
2013-06-01 10:50 | 5428.4309 | 5395.1377 | 5343.6814 | 143.5713 | 171.4752 | 5400.7839 | 153.0639 | 104.2477 | 2013-06-01 10:50 | 226.0818 | 216.9613 | 206.6451 | 100.5808 | 287.0049 | 202.53 | 84.5226 | 278.5089

## Table H12,13 Study Steps
| Source: | \Data\PaR Inputs\PaR Study Set-ups.xlsx
Table H.13 - Wind Integration Cost Simulations in PaR, 2012 WIS
| PaR Model Simulation | Forward Term | Load | Wind Profile | Incremental Reserve | Day-ahead Forecast Error
Regulating Margin Reserve Cost Runs
| 1 | 2015 | 2015 Load Forecast | Expected Profile | No | None
| 2 | 2015 | 2015 Load Forecast | Expected Profile | Yes | None
Regulating Margin Cost = System Cost from PaR Simulation 2 less System Cost from PaR Simulation 1
System Balancing Cost Runs
| 3 | 2015 | 2013 Day-ahead Forecast | 2013 Day-ahead Forecast | Yes | None
| 4 | 2015 | 2013 Actual | 2013 Day-ahead Forecast | Yes | For Load
| 5 | 2015 | 2013 Actual | 2013 Actual | Yes | For Load and Wind
Load System Balancing Cost = System Cost from PaR simulation 4 (which uses the unit commitment from
Simulation 3) less system cost from PaR simulation 3
Wind System Balancing Cost = System Cost from PaR simulation 5 (which uses the unit commitment from
Simulation 4) less system cost from PaR simulation 4
Table H.12 - Wind Integration Cost Simulations in PaR
| PaR Model Simulation | Forward Term | Load | Wind Profile | Incremental Reserve | Day-ahead Forecast Error | Comments
Regulating Margin Reserve Cost Runs
| 1 | 2015 | 2015 Load Forecast | Expected Profile | Load | None
| 2 | 2015 | 2015 Load Forecast | Expected Profile | Load and Wind | None
Regulating Margin Cost = System Cost from PaR Simulation 2 less System Cost from PaR Simulation 1
System Balancing Cost Runs
| 3 | 2015 | 2013 Day-ahead Forecast | 2013 Day-ahead Forecast | Yes | None | Commit units based on day-ahead load forecast, and day-ahead wind forecast
| 4 | 2015 | 2013 Actual | 2013 Actual | Yes | For Load and Wind | Apply commitment from Simulation 3
| 5 | 2015 | 2013 Actual | 2013 Day-ahead Forecast | Yes | None | Commit units based on actual Load, and day-ahead wind forecast
| 6 | 2015 | 2013 Actual | 2013 Actual | Yes | For Wind | Apply commitment from Simulation 5
| 7 | 2015 | 2013 Actual | 2013 Actual | Yes | None | Commit units based on actual Load, and actual wind forecast
Load System Balancing Cost = System Cost from PaR Simulation 4, which uses the unit commitment from Simulation 3 based on day-ahead
forecast load (and day-ahead wind) less System Cost from PaR Simulation 6, which uses the unit commitement from Simulation 5
based on actual load (and day-ahead wind)
Wind System Balancing Cost = System Cost from PaR Simulation 6, which uses the unit commitment from Simulation 5 based on day-ahdead
wind (and actual load) less System Cost from PaR Simulation 7, which commits units based on actual wind (and actual load)

## Table H.16 Gas&Power Prices
Source: | Tbl H.16 2014 WI Market & Gas Prices.xlsx
Table H.16 - Average Natural Gas and Electricity Prices Used in the 2012 and 2014 Wind Integration Studies
Study | Palo Verde High Load Hour Power ($/MW) | Palo Verde Low Load Hour Power ($/MW) | Opal Natural Gas ($/MMBtu)
2012 WIS | 37.05 | 25.74 | 3.43
2014 WIS | 39.13 | 29.31 | 3.88
The Study uses the December 31, 2013 OFPC official forward price curve.

## Fig H.7AVG Hrly Wind Reserves
Source: | \Data\PaR Inputs\Monthly vs. Hourly Reserve Requirements (With EIM Benefit).xlsx
Figure H.7 – Average Hourly Wind Reserves for 2013, MW

## Table H.17 Monthly Reserves
| Source: | \Data\PaR Inputs\Monthly vs Hourly Reserve Requirements (No EIM Benefit).xlsx
\Data\PaR Inputs\Hourly vs Monthly Combined Reserve Requirements.xlsx
Table H.17 - Total Load and Wind Monthly Reserves, Seperating Regulating and
Following Reserves (MW)
| Combined (MW) |  | Regulating |  | Following |  | Total (MW)
| West | East | West | East | West | East | West | East
Jan | 237.6014 | 400.2691 | 107.2292 | 195.7621 | 211.1328 | 353.8883 | 318.362 | 549.6504
Feb | 212.0266 | 363.1172 | 99.9335 | 181.714 | 187.2105 | 317.8944 | 287.1439 | 499.6084
Mar | 219.2206 | 356.5933 | 96.7348 | 179.3503 | 202.1024 | 313.0999 | 298.8372 | 492.4502
Apr | 239.802 | 422.3333 | 122.571 | 224.0128 | 208.2985 | 362.2186 | 330.8695 | 586.2315
May | 191.9722 | 399.6664 | 84.3003 | 205.0244 | 179.6906 | 347.8727 | 263.9909 | 552.8971
Jun | 182.8621 | 462.3757 | 69.9355 | 240.3174 | 179.1212 | 392.6507 | 249.0567 | 632.9681
Jul | 218.6824 | 427.2908 | 87.7013 | 180.3963 | 205.9956 | 391.4095 | 293.6969 | 571.8059
Aug | 219.788 | 427.6795 | 90.398 | 187.557 | 205.6854 | 388.3973 | 296.0834 | 575.9543
Sep | 209.5817 | 392.2323 | 99.5518 | 171.3255 | 187.5483 | 361.4471 | 287.1 | 532.7725
Oct | 152.979 | 335.28 | 74.6923 | 159.4695 | 130.9526 | 301.4808 | 205.6449 | 460.9503
Nov | 300.5922 | 437.7284 | 165.1621 | 228.1674 | 248.6103 | 375.3238 | 413.7724 | 603.4912
Dec | 274.2605 | 433.1649 | 121.5517 | 216.375 | 251.3342 | 375.1264 | 372.8859 | 591.5014