## Table I.1
Table 1
DSM
PRM (%) | Maximum | Capacity at System Peak | SCCT | CCCT | Total
10 | 1028.66 | 372.22 | 976.043 | 420.036 | 1768.299
11 | 1017.02 | 363.37 | 1157.043 | 420.036 | 1940.449
12 | 1019.83 | 365.45 | 1259.181 | 420.036 | 2044.667
13 | 1032.43 | 375.33 | 1259.181 | 420.036 | 2054.547
14 | 1017.02 | 363.39 | 1440.181 | 420.036 | 2223.607
15 | 1043.3 | 383.62 | 1440.181 | 420.036 | 2243.837
16 | 1009.81 | 357.96 | 1602.247 | 420.036 | 2380.243
17 | 1064.62 | 396.56 | 1611.714 | 420.036 | 2428.31
18 | 1017.02 | 363.37 | 1792.714 | 420.036 | 2576.12
19 | 1106.87 | 424.21 | 1792.714 | 420.036 | 2636.96
20 | 1095.92 | 415.92 | 1995.83 | 420.036 | 2831.786

## Table I.2-3, and Figures I.2-4
Table 2 | Simulated | [5 empty] | Table 3 | Fitted
| Before NWPP Adjustment |  |  | After NWPP Adjustment |  |  |  | Before NWPP Adjustment |  |  | After NWPP Adjustment
PRM (%) | EUE (GWh) | LOLH (Hour) | Modeled Loss of Load Episodes | EUE (GWh) | LOLH (Hour) | Modeled Loss of Load Episodes | PRM (%) | EUE (GWh) | LOLH (Hour) | Modeled Loss of Load Episodes | EUE (GWh) | LOLH (Hour) | Modeled Loss of Load Episodes
10 | 300.8227 | 2.5997 | 0.86743 | 200.4493 | 1.7323 | 0.48 | 10 | 293.69 | 2.7801 | 0.8965 | 198.27 | 1.8837 | 0.5222
11 | 182.5898 | 2.0334 | 0.74314 | 115.86 | 1.2903 | 0.40971 | 11 | 210.5817 | 2.0488 | 0.66499 | 141.9379 | 1.3839 | 0.38288
12 | 197.1483 | 1.7766 | 0.50371 | 141.2505 | 1.2729 | 0.29457 | 12 | 161.9664 | 1.6211 | 0.52956 | 108.9858 | 1.0916 | 0.30138
13 | 121.8646 | 1.5117 | 0.43371 | 86.9014 | 1.078 | 0.28571 | 13 | 127.4733 | 1.3176 | 0.43348 | 85.6059 | 0.88418 | 0.24355
14 | 83.8839 | 1.2406 | 0.35486 | 59.8895 | 0.88571 | 0.25086 | 14 | 100.7184 | 1.0821 | 0.35895 | 67.471 | 0.7233 | 0.1987
15 | 98.388 | 1.1934 | 0.302 | 73.4907 | 0.89143 | 0.22371 | 15 | 78.858 | 0.88979 | 0.29805 | 52.6537 | 0.59184 | 0.16206
16 | 31.7996 | 0.33514 | 0.20229 | 12.606 | 0.13286 | 0.044286 | 16 | 60.3754 | 0.72716 | 0.24657 | 40.1259 | 0.4807 | 0.13107
17 | 68.4055 | 0.45829 | 0.18086 | 41.41 | 0.27743 | 0.068857 | 17 | 44.365 | 0.58629 | 0.20197 | 29.2738 | 0.38442 | 0.10423
18 | 17.4209 | 0.304 | 0.12143 | 10.4624 | 0.18257 | 0.052 | 18 | 30.2428 | 0.46203 | 0.16263 | 19.7016 | 0.2995 | 0.080558
19 | 17.2062 | 0.40143 | 0.184 | 9.3195 | 0.21743 | 0.078286 | 19 | 17.61 | 0.35087 | 0.12744 | 11.1389 | 0.22354 | 0.05938
20 | 12.7953 | 0.26943 | 0.122 | 7.0015 | 0.14743 | 0.043143 | 20 | 6.1824 | 0.25032 | 0.095603 | 3.3931 | 0.15482 | 0.040223
w/ NWPP
Figure 2
Figure 3
Figure 4

## Table I.4
$ Thousands
Table 4
PRM (%) | System Variable Costs | DSM Run-Rate Costs | Up-front Capital & Run-rate Fixed Costs | Total Costs
10 | 1292361 | 34498 | 237119 | 1563978
11 | 1292341 | 32177 | 256251 | 1580769
12 | 1288956 | 32838 | 276790 | 1598584
13 | 1287921 | 34919 | 275976 | 1598816
14 | 1289097 | 32181 | 295108 | 1616386
15 | 1287021 | 38644 | 295108 | 1620773
16 | 1289396 | 30544 | 314025 | 1633965
17 | 1284925 | 44903 | 314133 | 1643961
18 | 1289300 | 32177 | 333265 | 1654742
19 | 1284132 | 143492 | 334144 | 1761768
20 | 1283763 | 141192 | 363042 | 1787997

## Table I.5, Figure I.5
Table 5
PRM | Fitted EUE | Total Costs | Reduction in Fitted EUE from EUE at 10% PRM After NWPP Adjustment | Reduction in Total System Cost from Cost at 10% PRM | Incremental Cost of EUE Relative to 10% PRM
(%) | (GWh) | ($000) | (GWh) | ($000) | ($/MWh) of EUE
10 | 198.27 | 1563978
11 | 141.9379 | 1580769 | 56.3321 | 16791 | 298.0718
12 | 108.9858 | 1598584 | 89.2842 | 34606 | 387.5937
13 | 85.6059 | 1598816 | 112.6641 | 34838 | 309.2199
14 | 67.471 | 1616386 | 130.799 | 52408 | 400.6758
15 | 52.6537 | 1620773 | 145.6163 | 56795 | 390.0319
16 | 40.1259 | 1633965 | 158.1441 | 69987 | 442.552
17 | 29.2738 | 1643961 | 168.9962 | 79983 | 473.2828
18 | 19.7016 | 1654742 | 178.5684 | 90764 | 508.2869
19 | 11.1389 | 1761768 | 187.1311 | 197790 | 1056.9596
20 | 3.3931 | 1787997 | 194.8769 | 224019 | 1149.5408
Figure 5

## NWPP Adj
2017
PRM (%) | Simulated Energy Not Served (GWh) | Simulated Expected Loss of Load Hours | Simulated Loss of Load Episodes | Energy Served through Reserve Sharing (GWh) | EUE (GWh) | LOLH
| G | H | O | G / H * O | N = G - R | H - O
10 | 300.8227 | 2.5997 | 0.86743 | 100.3734 | 200.4493 | 1.7323
11 | 182.5898 | 2.0334 | 0.74314 | 66.7298 | 115.86 | 1.2903
12 | 197.1483 | 1.7766 | 0.50371 | 55.8978 | 141.2505 | 1.2729
13 | 121.8646 | 1.5117 | 0.43371 | 34.9632 | 86.9014 | 1.078
14 | 83.8839 | 1.2406 | 0.35486 | 23.9944 | 59.8895 | 0.88571
15 | 98.388 | 1.1934 | 0.302 | 24.8973 | 73.4907 | 0.89143
16 | 31.7996 | 0.33514 | 0.20229 | 19.1936 | 12.606 | 0.13286
17 | 68.4055 | 0.45829 | 0.18086 | 26.9954 | 41.41 | 0.27743
18 | 17.4209 | 0.304 | 0.12143 | 6.9585 | 10.4624 | 0.18257
19 | 17.2062 | 0.40143 | 0.184 | 7.8867 | 9.3195 | 0.21743
20 | 12.7953 | 0.26943 | 0.122 | 5.7939 | 7.0015 | 0.14743