## References
Appendix N referenced values
| 3 | if in hour 19 on January 22nd there are three iterations with Energy Not Served (ENS) out of a total of 500 iterations
| 0.6% | then the LOLP for that hour would be 0.6 percent
| 57.6% | In the example noted above, the sum of LOLP among all winter hours is 58 percent
| 1.042% | The weighting factor for hour 19 on January 22nd would be 1.0417 percent
| 0.4271% | its weighted annual capacity contribution for that hour would be 0.4271 percent
| 288 | There are 288 winter ENS iteration-hours
| 5832 | out of total of 5,832 winter hours
| 579 | There are 579 summer ENS iteration-hours
| 2928 | out of total of 2,928 summer hours
| 115.8% | the sum of LOLP for the summer is 579 / 500 = 116 percent

## Table N.1
Nameplate Capacity (MW)
Study | Wind | Solar
No wind or solar | 0 | 0
No wind | 0 | 2217.67
No solar | 3722.235 | 0
Initial Portfolio | 3722.235 | 2217.67
Capacity Contribution of Initial Portfolio
MW | 851.644 | 955.435
% | 22.88% | 43.08%
Capacity Contribution of Incremental Resources
+1000 MW | 14.64% | 14.58%
+2000 MW | 11.74% | 2.306%
+3000 MW | 5.931% | 0%
+4000 MW | 0.7897% | 0%

## Table N.2-N.5
Table N.2 – Initial Capacity Contribution Values for Wind, Solar, and Storage
|  | Capacity Factor (%) | Capacity Contribution (%)
| IRP: |  | 2017 | 2019 | 2019 | 2019 | 2019
| Summer/Winter: | Annual | Annual | S | W | S | W
| Solar |  |  | Block 1 |  | Block 2
| Idaho Falls, ID | 27.7% | 59.67% | 26.81% | 6.029% | 4.137% | 0.9303% | IdahoF50_23
| Lakeview, OR | 29.29% | 64.8% | 36.3% | 6.783% | 5.601% | 1.047% | Lakeview50_23
| Milford, UT | 32.08% | 59.67% | 19.77% | 15.35% | 3.051% | 2.368% | Milford50_23
| Yakima, WA | 25.37% | 64.8% | 34.86% | 4.042% | 5.379% | 0.6237% | Yakima50_23
| Rock Springs, WY | 29.51% | 59.67% | 22.02% | 10.26% | 3.398% | 1.583% | RockSprings50_23
| Wind |  |  | Block 1 |  | Block 2
| Pocatello, ID | 37.05% | 15.78% | 19.57% | 24.88% | 4.49% | 5.71% | Pocatello, ID
| Arlington, OR | 37.05% | 11.78% | 37.35% | 15.62% | 8.57% | 3.584% | Arlington, OR
| Monticello, UT | 29.45% | 15.78% | 13.84% | 19% | 3.176% | 4.359% | Monticello, UT
| Goldendale, WA | 37.05% | 11.78% | 37.36% | 14.99% | 8.574% | 3.439% | Goldendale, WA
| Medicine Bow, WY | 43.62% | 15.78% | 16.82% | 38.49% | 3.859% | 8.832% | Medicine Bow, WY
Stand-alone Storage
| 2 hour duration |  |  | 66.63% | 84.51% |  |  | Li-Ion 2hr
| 4 hour duration |  |  | 90.67% | 98.96% |  |  | Li-Ion 4hr
| 9 hour duration |  |  | 100% | 100%
Table N.3 – Initial Capacity Contribution Values for Wind and Solar Combined with Storage
|  | Capacity Factor (%) | Capacity Contribution (%)
| IRP: | n/a | 2019 | 2019 | 2019 | 2019
| Summer/Winter: | Annual | S | W | S | W
| Solar & Storage |  | Block 1 |  | Block 2
| Idaho Falls, ID | 27.7% | 48.41% | 30.73% | 25.74% | 25.63%
| Lakeview, OR | 29.29% | 57.61% | 31.53% | 26.92% | 25.79%
| Milford, UT | 32.08% | 41.77% | 39.71% | 25.05% | 26.73%
| Yakima, WA | 25.37% | 56.12% | 28.79% | 26.64% | 25.37%
| Rock Springs, WY | 29.51% | 44.14% | 34.99% | 25.52% | 26.32%
| Wind & Storage |  | Block 1 |  | Block 2
| Pocatello, ID | 37.05% | 41.96% | 47.28% | 26.89% | 28.11%
| Arlington, OR | 37.05% | 54.56% | 39.94% | 25.78% | 27.9%
| Monticello, UT | 29.45% | 36.5% | 43.69% | 25.84% | 29.06%
| Goldendale, WA | 37.05% | 55.06% | 39.32% | 26.27% | 27.78%
| Medicine Bow, WY | 43.62% | 39.39% | 57.44% | 26.43% | 27.78%
Table N.4 – Final CF Method Capacity Contribution Values for Wind, Solar, and Storage
[11 empty] | Capacity Factor (%) | Capacity Contribution (%)
[10 empty] | Summer/Winter: | Annual | S | W
Solar
[10 empty] | Idaho Falls, ID | 27.7% | 12.4% | 12.84% | Solar_IRP_ID_ST
[10 empty] | Lakeview, OR | 29.29% | 14.87% | 13.96% | Solar_IRP_OR_ST
[10 empty] | Milford, UT | 32.08% | 9.93% | 22.94% | Solar_IRP_UT_ST
[10 empty] | Yakima, WA | 25.37% | 12.4% | 9.636% | Solar_IRP_YK_ST
[10 empty] | Rock Springs, WY | 29.51% | 11.11% | 18.7% | Solar_IRP_WY_ST
Wind
[10 empty] | Pocatello, ID | 37.05% | 19.11% | 27.18% | Wind_Goshen_W2
[10 empty] | Arlington, OR | 37.05% | 57.46% | 20.83% | Wind_I_OR
[10 empty] | Monticello, UT | 29.45% | 17.94% | 21.55% | Wind_I_UT
[10 empty] | Goldendale, WA | 37.05% | 56.77% | 21.22% | Wind_I_WA
[10 empty] | Medicine Bow, WY | 43.62% | 12.71% | 34.79% | Wind_I_WYAE
Stand-alone Storage
[10 empty] | 2 hour duration |  | 77.83% | 89.03%
[10 empty] | 4 hour duration |  | 93.93% | 100%
[10 empty] | 9 hour duration |  | 97.91% | 100%
Table N.5 – Final CF Method Capacity Contribution Values for Wind and Solar Combined with Storage
[11 empty] | Capacity Factor (%) | Capacity Contribution (%)
[10 empty] | Summer/Winter: | Annual | S | W
Solar & Storage
[10 empty] | Idaho Falls, ID | 27.7% | 32.69% | 37.49% | Solar_IRP_ID_ST
[10 empty] | Lakeview, OR | 29.29% | 35.16% | 38.61% | Solar_IRP_OR_ST
[10 empty] | Milford, UT | 32.08% | 30.22% | 47.59% | Solar_IRP_UT_ST
[10 empty] | Yakima, WA | 25.37% | 32.69% | 34.28% | Solar_IRP_YK_ST
[10 empty] | Rock Springs, WY | 29.51% | 31.4% | 43.35% | Solar_IRP_WY_ST
Wind & Storage
[10 empty] | Pocatello, ID | 37.05% | 38.37% | 50.12% | Wind_Goshen_W2
[10 empty] | Arlington, OR | 37.05% | 76.73% | 43.77% | Wind_I_OR
[10 empty] | Monticello, UT | 29.45% | 37.2% | 44.49% | Wind_I_UT
[10 empty] | Goldendale, WA | 37.05% | 76.03% | 44.16% | Wind_I_WA
[10 empty] | Medicine Bow, WY | 43.62% | 31.97% | 57.73% | Wind_I_WYAE