Report to: Utah Public Service Commission

## Electric Service Reliability - Major Event Report

# Event Date(s):		August 21-23, 2003

Date Submitted:		September 24, 2003

Affected Locations:		Ogden, Tremonton

Exclude from Performance Reports: 		Yes

Report Prepared by:		Diane DeNuccio

Report Approved by:		Heidi Caswell

Event Description:	Severe thunderstorms passed through Utah extending into Idaho and some of our Wyoming territory beginning Thursday, August 21, bringing lightning, marble-sized hail and torrential rains to many areas. Severe winds (maximum sustained winds exceeding 35 mph and newspapers quoting weather sources reported gusts over 100 mph) toppled trees, power poles and cargo-laden semi-trailers on I-80.  Urban and small stream flash flood warnings were in effect.  Roads in some areas were closed, some under water, hampering transit time for restoration personnel.  Reports in local newspapers described the severe storm as “monsoonal”.

The storm interrupted service to approximately 200 feeders.  The company also sustained damage to both its transmission and distribution system, including substation and line equipment.   Transmission lines in western Wyoming impacted by the storm were left out of service until the storm passed to prevent further damage and minimize system instability.

Company crews from American Fork to Rexburg, as well as contractor crews, responded quickly and worked through very tough conditions to restore power.

PacifiCorp is requesting designation of this storm and its consequences to be classified as a “Major Event” for exclusion from network performance reporting.   This major event exceeded the design and operational limits of the system, resulting in damage to transmission and distribution facilities, and caused sustained interruptions to more than 10% of customers in each of six affected operating areas.

Total Customer Minutes Lost = 15,960,533

Total Sustained Incidents = 469

Total Sustained Customers Off = 104,708  (14% overall, percent by area in attached report)

Resources Utilized:

Company 		22

Contract 		14

Tree 			8

Transmission 		5

Troubleman   		21

Support 		6

Restoration Problems:	Outage restoration efforts were hampered by closed roads, areas of flooding and severe winds.  The wide-reaching impact of the storms across multiple operating areas limited our ability to pull in additional resources from surrounding areas to provide restoration assistance as we would do when a smaller area is affected by a major event.  Contract crews were utilized.  Protracted transit times contributed to the duration of outages in this event.

Damage Cost:

Expense:   $259,120

Capital:    	$70,109

TOTAL: 	 $329,229

SAIDI, SAIFI, MAIFI Report:  Attached

|  |  |  | Customer Analysis |  |  |  |  | Customers Restored by Intervals |  |  |  | Major Event Only |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| UTAH | Sustained Customers Off | % Sustained Customers Off | CML | Number of Sustained Interruptions | Average Customer Count | 5 Min or Less | > 5 Min and <3 Hrs | >= 3 Hrs and <= 24 Hrs | > 24 Hrs | % Sustained Customers Restored < 3 Hrs | SAIDI | SAIFI | MAIFI |
| Event Total | 104,708 | 14% | 15,960,533 | 469 | 742,708 | 9,312 | 78,100 | 35,416 | 144 | 69% | 21.49 | 0.14 | 0.01 |
| AMERICAN FORK | 6,412 | 10% | 166,550 | 31 | 64,756 | 5 | 6,386 | 26 | 0 | 100% | 2.572 | 0.099 | 0.000 |
| LAYTON | 25,951 | 46% | 5,128,788 | 47 | 56,996 | 515 | 13,636 | 15,824 | 0 | 46% | 89.985 | 0.455 | 0.009 |
| OGDEN | 13,599 | 15% | 2,690,866 | 81 | 92,133 | 470 | 7,777 | 6,647 | 127 | 53% | 29.206 | 0.148 | 0.005 |
| SLC METRO | 33,102 | 16% | 2,504,027 | 174 | 203,243 | 5,945 | 32,699 | 3,014 | 0 | 92% | 12.320 | 0.163 | 0.029 |
| SMITHFIELD | 14,036 | 70% | 2,507,381 | 52 | 19,945 | 3 | 10,563 | 3,473 | 0 | 75% | 125.715 | 0.704 | 0.000 |
| TREMONTON | 11,608 | 147% | 2,962,921 | 84 | 7,905 | 2,374 | 7,039 | 6,432 | 17 | 52% | 374.816 | 1.468 | 0.300 |

|  | Customers Interrupted by Date |
| --- | --- |
|  | 8/21/03 0:56 | 8/23/03 21:37 |
| Date | Sustained Customers Off | % Sustained Customers Off | CML | Number of Sustained Interruptions |
| 8/21/2003 | 27,258 | 26% | 1,754,072 | 114 |
| 8/22/2003 | 75,944 | 73% | 13,838,776 | 283 |
| 8/23/2003 | 1,506 | 1% | 367,685 | 72 |