MEMORANDUM

To:		Public Service Commission

From:		Division of Public Utilities

Constance White, Director

Energy Section

Artie Powell, Energy Section Manager

Charles Peterson, Technical Consultant

Abdinasir Abdulle, Technical Consultant

Date:		November 9, 2006

Ref:		Docket Nos. 06-035-107 and 06-035-108

RECOMMENDATIONS

The Division recommends that the Commission approve the Company’s application for a major event exclusion of the events that took place on July 26, 2006 (Event 13) and August 1, 2006 (Event 14).  The SAIDI values for both events exceeded the threshold that defines a major event under the IEEE’s 2.5 Beta methodology adopted by the Commission in Docket No. 98-2035-04.

EVENT DESCRIPTION

Event 13

On July 26, 2006, a thunderstorm with high winds swept through Salt Lake City Metro, Jordan Valley, Ogden, and American Fork operating areas causing extensive damage to the system.  The damage included approximately 1,500 feet of conductors, 5 distribution poles, 2 transmission poles, 2 transformers, and 9 cross-arms being replaced.  The Company’s regular crews were augmented with contract crews and Company crews from other operating areas.  The event resulted in 39,974 customers experiencing sustained outage.  The damage was estimated to be $100,000, divided between $40,000 for labor and $60,000 for equipment.

Event 14

On August 1, 2006, a thunderstorm with microburst winds (gusts of 92 mph), heavy rain, lightning and hail moved into 16 Utah operating districts.  These districts are listed in the filing.  The storm resulted in hundreds of tree and dozens of power poles taken down and tree limbs flying into conductors.  This resulted in 54,298 customers experiencing sustained interruption of power supply.  The Company’s regular crews were augmented with contract crews and crews including resources from Idaho.  The damage was estimated to be $500,000 divided between $400,000 for labor and $100,000 for equipment.

PROCEDURE

To determine whether the events of July 26, 2006 and August 1, 2006 were major events the Division followed the IEEE 1366-2003 definition of major event.  The Commission adopted this new methodology, commonly referred as the 2.5 Beta method, in Docket No. 98-2035-04.  The IEEE 1366-2003 defines a Major Event as “an event that exceeds reasonable design and or operational limits of the electric power system.  A Major Event includes at least one Major Event Day”.  IEEE 1366-2003 defines a Major Event Day as “a day in which the system SAIDI exceeded a threshold value, TMED.”  A Major event Day is simply a day in which the reliability of the distribution system is much worse than normal.  The 2.5 Beta method allows the segmentation of reliability data into normal and abnormal categories, based on the identification of outlier events that cause Major Event Days.  Given that the daily SAIDI measures follow a log-normal distribution, the probability of a day being defined as a major event day is less than 1%.  The expected number of major events days is 2.3 per year.

FINDINGS

For the 2.5 Beta Method to be valid, the daily SAIDI data must follow a log-normal distribution.  That is, the log of the daily SAIDI data must follow a normal distribution.  Using the daily SAIDI provided by the Company (from April 2001 to March 2006), the Division performed a normality test to determine if, under normal conditions, the natural log of PacifiCorp’s daily SAIDI values approximate a normal distribution (testing if the daily SAIDI values have log-normal distribution will lead to the same conclusion).

To implement the test, the Division used a Box-and-Whisker plot to identify any outliers in the data set.  SAIDI values determined to be outliers were removed from the data set.  Removing the outliers was essential to ensure that the remaining data represented “normal” operating conditions.  To test for normality, the Division used the Kolmogorov-Smirnov normality tests.  The null hypothesis tested was that the natural log of PacifiCorp’s daily SAIDI values is normally distributed.  The Kolmogorov-Smirnov failed to reject the null hypothesis (at p<0.01).  Hence, based on the results of the Kolmogrov-Smirnov normality tests, the Division concludes that, under normal conditions, the natural log of PacifiCorp’s daily SAIDI values are normally distributed and the use of the 2.5 Beta Method is justified.

Based on the Company’s calculations, which were subsequently verified by the Division, the major event threshold (TMED) was 9.9.  The TMED, is calculated using the following procedure:

- Assemble the preceding three to five years of daily SAIDI values,

- Remove from the data set any day in which the daily SAIDI value was zero,

- Take the natural log of each of the daily SAIDI values,

- Calculate the mean, (, and the standard deviation, (, of the natural logs of the daily SAIDI values, and

- Calculate the threshold, .

According to the new definition of a major event any daily SAIDI value that exceeds 9.9 is considered a major event.  The Company’s Utah SAIDI value for July 26, 2006 and August 1, 2006 (Events 13 and 14) were 11.01 and 22.03, respectively.  Therefore, the events of July 26, 2006 and August 1, 2006 were major events and should be excluded from the network performance reporting.

Restoration Efforts

The graphical hourly analyses of Event 13 and Event 14, shown on Figures 1 and 2, respectively, show that the impact of the storms had been building up for a number of hours with the Company restoring customers as soon as practicable.  This is evidenced by the fact that the number of customers restored was tracing very closely the number of new customers out for the first few hours of the storms.  Viewed differently, this also means that as some customers were restored, some other customers were losing power.  The peak customers out for Event 13 took place in the hours between 5:00 to 6:00 p.m. and for event 14 around 10:00 am, whereas the peak customers restored took place at around 10:00 p.m. and 6:00 pm, respectively.  Approximately 63% of the customers that experienced sustained outage were restored within 3 hours and the remainder were restored within 24 hours.  Therefore, the Division concludes that the Company’s restoration efforts were adequate.

Figure 1.  Hourly analysis of event 13

Figure 2.  Hourly analysis of event 14

CC:	Rea Petersen, DPU

Doug Bennion, Rocky Mountain Power

Dan Gimble, CCS