MEMORANDUM

To:		Public Service Commission

From:		Division of Public Utilities

Philip Powlick, Director

Energy Section

Abdinasir Abdulle, Technical Consultant

Charles Peterson, Technical Consultant

Artie Powell, Energy Section Manager

Date:		March 10, 2008

Ref:		Docket No. 08-035-06 – Major Event 16 – December 7-10, 2007

RECOMMENDATIONS

The Division recommends that the Commission approve the attached Company’s modified application for a Major Event exclusion of the event that took place on December 7, 2007 through December 10, 2007 (Event 16).  The attached modified application should replace the initial application dated January 9, 2008.  The SAIDI value for the event exceeded the threshold that defines a Major Event under the IEEE’s 2.5 Beta methodology adopted by the Commission in Docket No. 98-2035-04.  The Division further recommends that the Company’s initial application and the accompanying spreadsheets be replaced with the modified application and the accompanying spreadsheets (modified on March 7, 2008).

EVENT DESCRIPTION

On December 7, 2007 a wet snow storm swept through Salt Lake City Metro, Jordan Valley, Richfield, and some other operating areas and continued through December 10, 2007.   This caused extensive damage to the system including damage to 86 substations and 153 circuits.  A complete list of the specific damages sustained by the system can be found in the Company’s application under the section “Damages.”  The event resulted in 43,501 customers experiencing sustained outage and 11,148,477 customer minutes being lost.  The damage was estimated to be $125,000, composed of $100,000 for labor and $25,000 for equipment.

PROCEDURE

To determine whether the event of December 7 through 9, 2007 was a Major Event the Division followed the IEEE 1366-2003 definition of a Major Event.  The Commission adopted this new methodology, commonly referred as the 2.5 Beta Method, in Docket No. 98-2035-04.  The IEEE 1366-2003 defines a Major Event as “an event that exceeds reasonable design and or operational limits of the electric power system.  A Major Event includes at least one Major Event Day”.  IEEE 1366-2003 defines a Major Event Day as “a day in which the system SAIDI exceeded a threshold value, TMED.”  A Major Event Day is simply a day in which the reliability of the distribution system is much worse than normal.  The 2.5 Beta Method allows the segmentation of reliability data into normal and abnormal categories, based on the identification of outlier events that cause Major Event Days.  Given that the daily SAIDI measures follow a log-normal distribution, the probability of a day being defined as a Major Event day is less than 1%.  The expected number of major events days is 2.3 per year.

FINDINGS

For the 2.5 Beta Method to be valid, the daily SAIDI data must follow a log-normal distribution.  That is, the log of the daily SAIDI data must follow a normal distribution.  Using the daily SAIDI provided by the Company (from January 1, 2002 to December 31, 2006), the Division performed a normality test to determine if, under normal operating conditions, the natural log of PacifiCorp’s daily SAIDI values approximate a normal distribution (testing if the daily SAIDI values have log-normal distribution will lead to the same conclusion).

To implement the test, the Division used a Box-and-Whisker plot to identify any outliers in the data set.  SAIDI values determined to be outliers were removed from the data set.  Removing the outliers was essential to ensure that the remaining data represented “normal” operating conditions.  To test for normality, the Division used the Kolmogorov-Smirnov normality test.  The null hypothesis tested was that the natural log of PacifiCorp’s daily SAIDI values are normally distributed.  The Kolmogorov-Smirnov failed to reject the null hypothesis (at p<0.01).  Hence, based on the result of the Kolmogrov-Smirnov normality test, the Division concludes that, under normal conditions, the natural log of PacifiCorp’s daily SAIDI values are normally distributed and the use of the 2.5 Beta Method is justified.

The Division calculated the Major Event threshold (TMED) as 9.4.  The TMED, is calculated using the following procedure:

- Assemble the preceding three to five years of daily SAIDI values,

- Remove from the data set any day in which the daily SAIDI value was zero,

- Take the natural log of each of the daily SAIDI values,

- Calculate the mean, (, and the standard deviation, (, of the natural logs of the daily SAIDI values, and

- Calculate the threshold, .

According to the new definition of a Major Event any daily SAIDI value that exceeds 9.4 is considered a Major Event.  The Company’s Utah SAIDI value for December 7 through 10, 2007 was 13.88.  Therefore, the event of December 7 through 10, 2007 was a Major Event and should be excluded from the network performance reporting.

Restoration Efforts

The graphical hourly analysis of Event 16 shown below shows that the impact of the storm had been building up for a number of hours with the Company restoring customers as soon as practicable.  This is evidenced by the fact that the cumulative customer minutes lost was relatively flat for the first few hours of the storm.  That means that as some customers were restored, some other customers were losing power.  The peak customers out took place around 10:00 a.m. in December 8, 2008.  Despite traffic congestion resulting from toppled trees and other access problems, approximately 66% of the customers that experienced a sustained outage were restored within between 5 minutes and 3 hours.  99% of the customers that experienced a sustained outage were restored within 24 hrs.

Customer Guarantee 1 (Restoring Supply After an Outage) requires that in the event of an outage, the Company will restore a customer’s electric supply within 24 hours of being notified except where, among other things, there is an inability to access the Company’s or the Customer’s facility for reasons beyond the Company’s control and where there is a major event.  Hence, since there was access problems as is described above, the Company could not be reasonably expected to restore power to all customers within 24 hours.  Therefore, given the available information, the Division concludes that the Company’s restoration efforts were adequate.

Figure 1.  Hourly analysis of event 16

CC:	Rea Petersen, DPU

Doug Bennion, RMP

Dave Taylor, RMP

Michel Beck, CCS

# Footnotes

A complete list of the affected operating areas can be found in the spreadsheets attached to the Company’s application.