MEMORANDUM

To:		Public Service Commission

From:		Division of Public Utilities

Philip Powlick, Director

Energy Section

Abdinasir Abdulle, Technical Consultant

Charles Peterson, Technical Consultant

Artie Powell, Energy Section Manager

Date:		May 7, 2008

Ref:		Docket No. 08-035-25 – Major Event 17 – January 4-5, 2008

RECOMMENDATIONS

The Division recommends that the Commission approve the Company’s application for a Major Event exclusion of the event that took place on January 4 through 5, 2008 (Event 17).  The System Average Interruption Duration Index (SAIDI) value for the event exceeded the threshold that defines a Major Event under the Institute of Electrical and Electronic Engineers’ (IEEE) 2.5 Beta methodology adopted by the Commission in Docket No. 98-2035-04.

EVENT DESCRIPTION

On January 4 through 5, 2008, hurricane force winds with rain followed by a wet snow storm swept through Salt Lake City Metro, Jordan Valley, Tooele, and some other operating areas  causing extensive damage to the system.  Among other damages to facilities, the Microburst (100 miles per hour) damaged 22 transmission poles (21 of these in Tooele), 7 distribution poles (6 of these in Tooele), 4 transformers, and 9 cross arms,.  All these facilities and 10,000 line feet of conductor had to be replaced.  The event resulted in 46,758 customers experiencing sustained outage and 12,910,816 customer minutes being lost.  The damage was estimated to be $600,000, composed of $450,000 for labor and $150,000 for equipment.

PROCEDURE

To determine whether the event of January 4 through 5, 2008 was a Major Event the Division followed the IEEE 1366-2003 definition of a Major Event.  The Commission adopted this new methodology, commonly referred as the 2.5 Beta Method, in Docket No. 98-2035-04.  The IEEE 1366-2003 defines a Major Event as “an event that exceeds reasonable design and or operational limits of the electric power system.  A Major Event includes at least one Major Event Day”.  IEEE 1366-2003 defines a Major Event Day as “a day in which the system SAIDI exceeded a threshold value, TMED.”  A Major Event Day is simply a day in which the reliability of the distribution system is much worse than normal.  The 2.5 Beta Method allows the segmentation of reliability data into normal and abnormal categories, based on the identification of outlier events that cause Major Event Days.  Given that the daily SAIDI measures follow a log-normal distribution, the probability of a day being defined as a Major Event day is less than 1%.  The expected number of major events days is 2.3 per year.

FINDINGS

For the 2.5 Beta Method to be valid, the daily SAIDI data must follow a log-normal distribution.  That is, the log of the daily SAIDI data must follow a normal distribution.  Using the daily SAIDI provided by the Company (from January 1, 2003 to December 31, 2007), the Division performed a normality test to determine if, under normal operating conditions, the natural log of PacifiCorp’s daily SAIDI values approximate a normal distribution (testing if the daily SAIDI values have log-normal distribution will lead to the same conclusion).

To implement the test, the Division used a Box-and-Whisker plot to identify any outliers in the data set.  SAIDI values determined to be outliers were removed from the data set.  Removing the outliers was essential to ensure that the remaining data represented “normal” operating conditions.  To test for normality, the Division used the Kolmogorov-Smirnov normality test.  The null hypothesis tested was that the natural log of PacifiCorp’s daily SAIDI values are normally distributed.  The Kolmogorov-Smirnov failed to reject the null hypothesis (at p<0.01).  Hence, based on the result of the Kolmogrov-Smirnov normality test, the Division concludes that, under normal conditions, the natural log of PacifiCorp’s daily SAIDI values are normally distributed and the use of the 2.5 Beta Method is justified.

The Division calculated the Major Event threshold (TMED) as 8.6.  The TMED, is calculated using the following procedure:

- Assemble the preceding three to five years of daily SAIDI values,

- Remove from the data set any day in which the daily SAIDI value was zero,

- Take the natural log of each of the daily SAIDI values,

- Calculate the mean, (, and the standard deviation, (, of the natural logs of the daily SAIDI values, and

- Calculate the threshold, .

According to the new definition of a Major Event, any daily SAIDI value that exceeds 8.6 is considered a Major Event.  The Company’s Utah SAIDI value for January 4 through 5, 2008 was 16.17.  Therefore, the event of January 4 through 5, 2008 was a Major Event and should be excluded from the network performance reporting.

Restoration Efforts

The graphical hourly analysis of Event 17 shown below shows that the impact of the storm had been building up for a number of hours with the Company restoring customers as soon as practicable.  This is evidenced by the fact that the cumulative customer minutes lost was relatively flat for the first few hours of the storm.  That means that as some customers were restored, some other customers were losing power.  The peak number of customers without service took place around 8:00 p.m.on January 4, 2008.  Despite traffic congestion resulting from toppled trees, approximately 59% of the customers that experienced a sustained outage were restored within between 5 minutes and 3 hours.  99% of the customers that experienced a sustained outage were restored within 24 hrs.

Customer Guarantee 1 (Restoring Supply After an Outage) requires that in the event of an outage, the Company will restore a customer’s electric supply within 24 hours of being notified except where, among other things, there is an inability to access the Company’s or the Customer’s facility for reasons beyond the Company’s control and where there is a major event.  Hence, since there were access problems as described above, the Company could not be reasonably expected to restore power to all customers within 24 hours.  Therefore, given the available information, the Division concludes that the Company’s restoration efforts were adequate.

Figure 1.  Hourly analysis of event 17

CC:	Rea Petersen, DPU

Doug Bennion, RMP

Dave Taylor, RMP

Michel Beck, CCS

# Footnotes

A complete list of the affected operating areas can be found in the spreadsheets attached to the Company’s application.