## 2016Complete Schedule
FL Replacement List
*This schedule is subject to revision based on ongoing risk, constructability, availability of materials, construction moritoriums, permitting issues, competing (co-located) civil projects and system constraints analyses.
April 2016
Line (Segment) | City/County | Footage | Scheduled

## FL6-a (hidden)
Line | FL6
Segment | a
Description | 3300 South to 7700 South
Length of Section | 6.18 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 75%
Pop. Dens | Med
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction, Longitudinal Seam Type and SMEs.
Back

## FL6-b (hidden)
Line | FL6
Segment | b
Description | 7800 South to 8000 South
Length of Section | .24 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 100%
Pop. Dens | Med
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction, Longitudinal Seam Type and SMEs.
Back

## FL6-c (hidden)
Line | FL6
Segment | c
Description | 8100 South to Sego Lilly Drive
Length of Section | 2.64 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 90%
Pop. Dens | Med
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction, Longitudinal Seam Type and SMEs.
Back

## FL6-d (hidden)
Line | FL6
Segment | d
Description | 10600 South to Wasatch BLVD
Length of Section | 1.22 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 45%
Pop. Dens | Med
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction, Longitudinal Seam Type and SMEs.
Back

## FL6-e (hidden)
Line | FL6
Segment | e
Description | 10600 South to Wasatch BLVD
Length of Section | 1.32 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 0%
Pop. Dens | Med
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | Year of Construction, Longitudinal Seam Type and SMEs.
Back

## FL6-f (hidden)
Line | FL6
Segment | f
Description | 13800 South to FL24
Length of Section | 1.32 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 0%
Pop. Dens | Med
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | Year of Construction and Longitudinal seam type.
Back

## FL24-a (hidden)
Line | FL24
Segment | a
Description | FL6 to Hog Hollow RD
Length of Section | 2.26 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 0%
Pop. Dens | MED to HIGH
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | Year of Construction and Longitudinal seam type.
Back

## FL24-b (hidden)
Line | FL24
Segment | b
Description | Hog Hollow RD to Ridge DR
Length of Section | 1.67 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 55%
Pop. Dens | Low
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction and Longitudinal seam type.
Back

## FL24-c (hidden)
Line | FL24
Segment | c
Description | Healy BLVD to Nielsen BLVD
Length of Section | 1.65 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 35%
Pop. Dens | MED
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction and Longitudinal seam type.
Back

## FL24-d (hidden)
Line | FL24
Segment | d
Description | Canyon RD to Jens Monson LN
Length of Section | 3.37 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 10%
Pop. Dens | LOW
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction and Longitudinal seam type.
Back

## FL24-e (hidden)
Line | FL24
Segment | e
Description | 850 North to 550 North
Length of Section | 1.95 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 90%
Pop. Dens | MED to HIGH
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Population density, Year of Construction and Longitudinal seam type.
Back

## FL24-f (hidden)
Line | FL24
Segment | f
Description | 1000 North to 800 North
Length of Section | 1.36 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 100%
Pop. Dens | MED to HIGH
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Population density, Year of Construction and Longitudinal seam type.
Back

## FL24-g (hidden)
Line | 24
Segment | g
Description | 800 North to End of FL24
Length of Section | 4.22 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 96%
Pop. Dens | HIGH
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Population density, Year of Construction and Longitudinal seam type.
Back

## FL34 (hidden)
Line | FL34
Segment | a
Description | 3400 South to 8000 South
Length of Section | 6.53 mi
Inservice Date | 1962-10-23
Long Seam Type | Unknown
HCA's | 85%
Pop. Dens | MED to HIGH
Diameter | 20"
Grade | x42
WT | 0.281
Comments: | Year of Construction, HCAs and Population Density.
Back

## FL13-a (hidden)
Line | FL13
Segment | a
Description | 6800 South to 6400 South
Length of Section | .63 mi
Inservice Date | 1952-12-19
Long Seam Type | Unknown
HCA's | 40%
Pop. Dens | LOW
Diameter | 12"
Grade | x42
WT | 0.25
Comments: | Year of Construction, HCAs and lack of pressure test records.
Back

## FL13-b (hidden)
Line | FL13
Segment | b
Description | 5370 West to 4400 West
Length of Section | 1.23 mi
Inservice Date | 1952-12-19
Long Seam Type | Unknown
HCA's | 45%
Pop. Dens | LOW
Diameter | 12"
Grade | x42
WT | 0.25
Comments: | Year of Construction, HCAs and lack of pressure test records.
Back

## FL13-c (hidden)
Line | FL13
Segment | c
Description | 3700 West to 2570 West
Length of Section | 1.1 mi
Inservice Date | 1952-12-19
Long Seam Type | Unknown
HCA's | 80%
Pop. Dens | LOW
Diameter | 12"
Grade | x42
WT | 0.25
Comments: | Year of Construction, HCAs and lack of pressure test records.
Back

## FL13-d (hidden)
Line | FL13
Segment | d
Description | I-215 to 900 West
Length of Section | 1.43 mi
Inservice Date | 1952-12-19
Long Seam Type | Unknown
HCA's | 100%
Pop. Dens | LOW
Diameter | 12"
Grade | x42
WT | 0.25
Comments: | Year of Construction, HCAs and lack of pressure test records.
Back

## FL8-a (hidden)
Line | FL8
Segment | a
Description | 1300 West to State Street
Length of Section | 2.37 mi
Inservice Date | 1958-09-16
Long Seam Type | LFERW
HCA's | 0%
Pop. Dens | MED to HIGH
Diameter | 6"
Grade | B
WT | 0.25
Comments: | HCAs, Year of Construction, Longitudinal seam type and lack of pressure test records.
Back

## FL8-b (hidden)
Line | FL8
Segment | b
Description | State Street to 1300 East
Length of Section | 1.9 mi
Inservice Date | 1953-10-05
Long Seam Type | LFERW
HCA's | 0%
Pop. Dens | MED to HIGH
Diameter | 6"
Grade | B
WT | 0.25
Comments: | HCAs, Year of Construction, Longitudinal seam type and lack of pressure test records.
Back

## FL21-4a (hidden)
Line | FL21-4
Segment | a
Description | 200 East to Medical Drive
Length of Section | 1.58 mi
Inservice Date | 1967-02-06
Long Seam Type | ERW
HCA's | 0%
Pop. Dens | HIGH
Diameter | 4"
Grade | B
WT | 0.219
Comments: | HCA and Population Density
Back

## FL21-4b (hidden)
Line | FL21-4
Segment | b
Description | 200 East to Medical Drive
Length of Section | .83 mi
Inservice Date | 1967-02-06
Long Seam Type | Unknown
HCA's | 100%
Pop. Dens | HIGH
Diameter | 12"
Grade | x42
WT | 0.25
Comments: | HCA and Population Density
Back

## FL42 (hidden)
Line | FL42
Segment
Description | FL26 to 1600 South
Length of Section | 3.12 mi
Inservice Date | 1966-12-08
Long Seam Type | Unknown
HCA's | 80%
Pop. Dens | LOW to MED
Diameter | 20"
Grade | x42
WT | 0.281
Comments: | HCAs.
Back

## FL42-3 (hidden)
Line | FL42-3
Segment
Description | 1450 West to 200 West
Length of Section | 1.16 mi/6125 ft
Inservice Date | 1966-12-03
Long Seam Type | Unknown
HCA's | 0%
Pop. Dens | MED
Diameter | 6"
Grade | x42
WT | 0.219
Comments: | HCAs and population density.
Back

## FL97 (hidden)
Line | FL97
Segment
Description | Moab
Length of Section | 3.81 mi
Inservice Date | 1963-01-01
Long Seam Type | Unknown
HCA's | 0%
Pop. Dens | LOW
Diameter | 4"
Grade | A24
WT | 0.154
Comments: | SMEs (Utah Gas line) and Lack of pressure test data.
Back

## FL110 (hidden)
Line | FL110
Segment
Description | Vernal
Length of Section | 42 mi
Inservice Date | 1974-02-18
Long Seam Type | ERW
HCA's | 0%
Pop. Dens | LOW
Diameter | 8"
Grade | x42
WT | 0.188
Comments: | SMEs (Utah Gas line)
Back

## FL89 (hidden)
Line | FL89
Segment
Description | Vernal
Length of Section | 3.71 mi
Inservice Date | 1956-02-21
Long Seam Type | Continuous
HCA's | 0%
Pop. Dens | LOW
Diameter | 4"
Grade | B
WT | 0.188
Comments: | SMEs (Utah Gas line)
Back

## FL98 (hidden)
Line | FL98
Segment
Description | Monticello
Length of Section | 12 mi
Inservice Date | 1956-02-21
Long Seam Type | Continuous
HCA's | 0%
Pop. Dens | LOW
Diameter | 4"
Grade | B
WT | 0.188
Comments: | SMEs (Utah Gas line)
Back