## 2016Complete Schedule
Change in HP Master List Footage
| A | C | D | B | J | K | C |  | D | E | G |  | F
2/
| Line (Segment) | Schedule Footage | ADD Est. 2013 Projects | 2013 Master List |  |  | Replaced / Retired |  | Mapping Update /Conflation | Data Corrections | Total Change |  | 2016 Master List
1 | FL4 | 27355 |  | 27355 |  |  |  |  | 534.41 |  | 534.41 |  | 27889.41
2 | FL6 | 72116 |  | 72116 | -51237 | -8826.5 | -60063.5 |  |  |  | -60063.5 |  | 12052
3 | FL8 (2013 project, not scheduled after 13) |  | 20477 | 20477 | -20344 | -54 | -20398 |  | -79 |  | -20477
4 | FL11 | 3460 |  | 3460 |  |  |  |  | -4 |  | -4 |  | 3456
5 | FL11-1(a) | 23141 |  | 23141 |  |  |  |  | -109 |  | -109 |  | 23032
6 | FL12 | 1457 |  | 1457 | [8 empty] | 1429
7 | FL12-1 | 5416 |  | 5416 | [8 empty] | 5563
8 | FL12-2 | 2456 |  | 2456 | [8 empty] | 2468
9 | Total FL12 | 9329 |  | 9329 |  |  |  |  | 131 |  | 131 |  | 9460
10 | FL13 | 46771 |  | 46771 |  |  |  |  | 540.5 |  | 540.5 |  | 47311.5
11 | FL14 | 18577 | 65646.38 | 84223.38 | -58099.38 |  | -58099.38 |  | 0 |  | -58099.38 |  | 26124
12 | FL15 | 52287 |  | 52287 | [8 empty] | 52475
13 | FL15-1 | 9807 |  | 9807 | [8 empty] | 9946
14 | FL15-2 | 50999 |  | 50999 | [8 empty] | 50811
15 | Total FL15 | 113093 |  | 113093 |  |  |  |  | 139 |  | 139 |  | 113232
16 | FL16 | 56231 |  | 56231 |  |  |  |  | -188.7 |  | -188.7 |  | 56042.3
17 | FL16-10 | 2430 |  | 2430 |  |  |  |  | -3 |  | -3 |  | 2427
18 | FL18 | 3129 |  | 3129 | -2397 | -46 | -2443 |  | -686 |  | -3129
19 | FL18-3 | 2159 |  | 2159 |  |  |  |  | 0 |  | 0 |  | 2159
20 | FL19 | 307 |  | 307 |  |  |  |  | 252 |  | 252 |  | 559
21 | FL20 (2013 project, not scheduled after 13) |  | 5800 | 5800 | -5358 | -200 | -5558 |  | -242 |  | -5800
22 | FL21 | 66951 |  | 66951 | [8 empty] | 72665
23 | FL21-10 | 3256 |  | 3256 | [8 empty] | 3217
24 | FL21-13 | 8654 |  | 8654 | [8 empty] | 7857.5
25 | FL21-19 | 5974 |  | 5974 | [8 empty] | 5943
26 | FL21-20 | 5570 |  | 5570 | [8 empty] | 5570
27 | FL21-4 | 14914 |  | 14914 | [8 empty] | 14917
28 | FL21-5 | 19512 |  | 19512 | [8 empty] | 19512
29 | FL21-50(a) | 1003 |  | 1003
30 | FL21-50(b) | 114755 |  | 114755 | [8 empty] | 110375
31 | Total FL21 | 240589 |  | 240589 |  | -1085 | -1085 |  | 553 |  | -532 |  | 240056.5
32 | FL22 | 33294 | 32104 | 65398 |  | -24656.5 | -24656.5 | 2/ | 32 |  | -24624.5 |  | 40773.5
33 | FL23 | 187153 |  | 187153 |  |  |  |  | 84 |  | 84 |  | 187237
34 | FL23-2 | 12309 |  | 12309 |  |  |  |  | -771.2 |  | -771.2 |  | 11537.8
35 | FL24 | 98043 |  | 98043 | -31.75 | -43416.94 | -43448.69 |  |  |  | -43448.69 |  | 54594.31
36 | FL26 | 1003 |  | 1003 | [8 empty] | 52367.7
37 | FL26 | 61615 |  | 61615
38 | Total FL 26 | 62618 |  | 62618 | -8047.8 | -2202 | -10249.8 |  |  |  | -10249.8 |  | 52367.7
39 | FL28(a) | 61715 |  | 61715 |  |  |  |  | -0.5 |  | -0.5 |  | 61714.5
40 | FL29 | 106156 |  | 106156 |  |  |  |  | -491.5 |  | -491.5 |  | 105664.5
41 | FL29-10 | 6305 |  | 6305 | [6 empty] | 0 |  | 6305
42 | FL32 | 15629 |  | 15629 | [6 empty] | 0 |  | 15629
43 | FL33 | 24506 |  | 24506 |  |  |  |  | -362 |  | -362 |  | 24144
44 | FL34 | 85221 |  | 85221 | -699.72 | -133.98 | -833.7 |  |  |  | -833.7 |  | 84386.8
45 | FL35(b) | 27421 |  | 27421 |  |  |  |  | 275 |  | 275 |  | 27696
46 | FL36(b) | 33826 | 16265 | 50091 | -18223.5 | -1480.5 | -19704 |  |  |  | -19704 |  | 30387
47 | FL38 | 103736 |  | 103736 | [5 empty] | 15913 | 15913 | 1/ | 119649
48 | FL41(b) | 9504 |  | 9504 | [8 empty] | 7149
49 | FL41(c) | 21436 |  | 21436 | [8 empty] | 22189
50 | Total FL 41 | 30940 | 13745 | 44685 | -15346.5 |  | -15346.5 |  |  |  | -15346.5 |  | 29338
51 | FL42 | 121073 |  | 121073 |  |  |  |  | 97.8 |  | 97.8 |  | 121170.8
52 | FL42-3 | 20520 |  | 20520 |  |  |  |  | 125 |  | 125 |  | 20645
53 | FL43 | 63903 |  | 63903 | [8 empty] | 64408.88
54 | FL43-3 | 94602 |  | 94602 | [8 empty] | 94041
55 | Total FL 43 | 158505 |  | 158505 |  |  |  |  | -55.12 |  | -55.12 |  | 158449.88
56 | FL45 | 24021 |  | 24021 | [6 empty] | 0 |  | 24021
57 | FL46 | 15138 |  | 15138 |  |  |  |  | 112 |  | 112 |  | 15250
58 | FL47 | 5022 |  | 5022 | [6 empty] | 0 |  | 5022
59 | FL48 | 6875 |  | 6875 |  |  |  |  | -43 |  | -43 |  | 6832
60 | FL50 (2013 project, not scheduled after 13) |  | 29077 | 29077 | -29065 | 0 | -29065 |  | -12 |  | -29077
61 | FL51 | 62046 |  | 62046 | [8 empty] | 6964
62 |  |  |  | 0 | [8 empty] | 54954
63 | Total FL 51 | 62046 |  | 62046 |  |  |  |  | -128 |  | -128 |  | 61918
64 | FL86-1 | 4004 |  | 4004 |  |  |  |  | -25 |  | -25 |  | 3979
65 | FL89 | 19400 |  | 19400 | [6 empty] | 0 |  | 19400
66 | FL97 | 14298 |  | 14298 | [5 empty] | 5600 | 5600 | 1/ | 19898
67 | FL98 | 63531 |  | 63531 | [6 empty] | 0 |  | 63531
68 | FL 11-2A | 2979 |  | 2979 | [8 empty] | 12182
69 | FL11-2 | 9389 |  | 9389
70 | Total FL120 Footage 3/ | 12368 |  | 12368 |  |  |  |  | -186 |  | -186 |  | 12182
71 | Total Footage | 2034360 |  | 2217474.38 | -208849.65 | -82101.42 | -290951.07 |  | -510.31 | 21513 | -269948.38 |  | 1947523.5
72 | Total Miles (Line 71 / 5280) | 3398303 |  | 419.9762 | -366462.3 | -155376.34 | -55.1044 |  | -0.09665 | 4.0744 | -480367.67 |  | 368.8491
1/ | 21,513 feet were excluded from the original master list for the following reasons. First, 15,913 feet were not properly queried on Feeder Line 38 and were omitted when the initial master list was generated. The Company found and corrected the error in the data prior to its 2015 Master List update. Additionally, 5,600 feet on Feeder Line 97 were originally recorded in the database with an incorrect installation date of 2001, the date the Company purchased the Utah Gas system, rather than 1963, the date the pipe was installed. This caused the footage to be excluded from the original schedule when the schedule was generated. The Company found this data entry error and corrected the installation date which increased the footage shown in Feeder Line 97 by 5,600 feet on the most recent schedule.
2/ | The retirement of 24,657 feet on FL22 was not included in the infrastructure tracker program because the project was for retirement only, not replacement under the Infrastructure Replacement Tracker.
3/ | FL-11-2 and FL11-2A have been combined and renamed to FL120

## FL6-a (hidden)
Line | FL6
Segment | a
Description | 3300 South to 7700 South
Length of Section | 6.18 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 75%
Pop. Dens | Med
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction, Longitudinal Seam Type and SMEs.
Back

## FL6-b (hidden)
Line | FL6
Segment | b
Description | 7800 South to 8000 South
Length of Section | .24 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 100%
Pop. Dens | Med
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction, Longitudinal Seam Type and SMEs.
Back

## FL6-c (hidden)
Line | FL6
Segment | c
Description | 8100 South to Sego Lilly Drive
Length of Section | 2.64 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 90%
Pop. Dens | Med
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction, Longitudinal Seam Type and SMEs.
Back

## FL6-d (hidden)
Line | FL6
Segment | d
Description | 10600 South to Wasatch BLVD
Length of Section | 1.22 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 45%
Pop. Dens | Med
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction, Longitudinal Seam Type and SMEs.
Back

## FL6-e (hidden)
Line | FL6
Segment | e
Description | 10600 South to Wasatch BLVD
Length of Section | 1.32 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 0%
Pop. Dens | Med
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | Year of Construction, Longitudinal Seam Type and SMEs.
Back

## FL6-f (hidden)
Line | FL6
Segment | f
Description | 13800 South to FL24
Length of Section | 1.32 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 0%
Pop. Dens | Med
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | Year of Construction and Longitudinal seam type.
Back

## FL24-a (hidden)
Line | FL24
Segment | a
Description | FL6 to Hog Hollow RD
Length of Section | 2.26 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 0%
Pop. Dens | MED to HIGH
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | Year of Construction and Longitudinal seam type.
Back

## FL24-b (hidden)
Line | FL24
Segment | b
Description | Hog Hollow RD to Ridge DR
Length of Section | 1.67 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 55%
Pop. Dens | Low
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction and Longitudinal seam type.
Back

## FL24-c (hidden)
Line | FL24
Segment | c
Description | Healy BLVD to Nielsen BLVD
Length of Section | 1.65 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 35%
Pop. Dens | MED
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction and Longitudinal seam type.
Back

## FL24-d (hidden)
Line | FL24
Segment | d
Description | Canyon RD to Jens Monson LN
Length of Section | 3.37 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 10%
Pop. Dens | LOW
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Year of Construction and Longitudinal seam type.
Back

## FL24-e (hidden)
Line | FL24
Segment | e
Description | 850 North to 550 North
Length of Section | 1.95 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 90%
Pop. Dens | MED to HIGH
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Population density, Year of Construction and Longitudinal seam type.
Back

## FL24-f (hidden)
Line | FL24
Segment | f
Description | 1000 North to 800 North
Length of Section | 1.36 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 100%
Pop. Dens | MED to HIGH
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Population density, Year of Construction and Longitudinal seam type.
Back

## FL24-g (hidden)
Line | 24
Segment | g
Description | 800 North to End of FL24
Length of Section | 4.22 mi
Inservice Date | 1948-08-19
Long Seam Type | LFERW
HCA's | 96%
Pop. Dens | HIGH
Diameter | 10"
Grade | x42
WT | 0.25
Comments: | HCAs, Population density, Year of Construction and Longitudinal seam type.
Back

## FL34 (hidden)
Line | FL34
Segment | a
Description | 3400 South to 8000 South
Length of Section | 6.53 mi
Inservice Date | 1962-10-23
Long Seam Type | Unknown
HCA's | 85%
Pop. Dens | MED to HIGH
Diameter | 20"
Grade | x42
WT | 0.281
Comments: | Year of Construction, HCAs and Population Density.
Back

## FL13-a (hidden)
Line | FL13
Segment | a
Description | 6800 South to 6400 South
Length of Section | .63 mi
Inservice Date | 1952-12-19
Long Seam Type | Unknown
HCA's | 40%
Pop. Dens | LOW
Diameter | 12"
Grade | x42
WT | 0.25
Comments: | Year of Construction, HCAs and lack of pressure test records.
Back

## FL13-b (hidden)
Line | FL13
Segment | b
Description | 5370 West to 4400 West
Length of Section | 1.23 mi
Inservice Date | 1952-12-19
Long Seam Type | Unknown
HCA's | 45%
Pop. Dens | LOW
Diameter | 12"
Grade | x42
WT | 0.25
Comments: | Year of Construction, HCAs and lack of pressure test records.
Back

## FL13-c (hidden)
Line | FL13
Segment | c
Description | 3700 West to 2570 West
Length of Section | 1.1 mi
Inservice Date | 1952-12-19
Long Seam Type | Unknown
HCA's | 80%
Pop. Dens | LOW
Diameter | 12"
Grade | x42
WT | 0.25
Comments: | Year of Construction, HCAs and lack of pressure test records.
Back

## FL13-d (hidden)
Line | FL13
Segment | d
Description | I-215 to 900 West
Length of Section | 1.43 mi
Inservice Date | 1952-12-19
Long Seam Type | Unknown
HCA's | 100%
Pop. Dens | LOW
Diameter | 12"
Grade | x42
WT | 0.25
Comments: | Year of Construction, HCAs and lack of pressure test records.
Back

## FL8-a (hidden)
Line | FL8
Segment | a
Description | 1300 West to State Street
Length of Section | 2.37 mi
Inservice Date | 1958-09-16
Long Seam Type | LFERW
HCA's | 0%
Pop. Dens | MED to HIGH
Diameter | 6"
Grade | B
WT | 0.25
Comments: | HCAs, Year of Construction, Longitudinal seam type and lack of pressure test records.
Back

## FL8-b (hidden)
Line | FL8
Segment | b
Description | State Street to 1300 East
Length of Section | 1.9 mi
Inservice Date | 1953-10-05
Long Seam Type | LFERW
HCA's | 0%
Pop. Dens | MED to HIGH
Diameter | 6"
Grade | B
WT | 0.25
Comments: | HCAs, Year of Construction, Longitudinal seam type and lack of pressure test records.
Back

## FL21-4a (hidden)
Line | FL21-4
Segment | a
Description | 200 East to Medical Drive
Length of Section | 1.58 mi
Inservice Date | 1967-02-06
Long Seam Type | ERW
HCA's | 0%
Pop. Dens | HIGH
Diameter | 4"
Grade | B
WT | 0.219
Comments: | HCA and Population Density
Back

## FL21-4b (hidden)
Line | FL21-4
Segment | b
Description | 200 East to Medical Drive
Length of Section | .83 mi
Inservice Date | 1967-02-06
Long Seam Type | Unknown
HCA's | 100%
Pop. Dens | HIGH
Diameter | 12"
Grade | x42
WT | 0.25
Comments: | HCA and Population Density
Back

## FL42 (hidden)
Line | FL42
Segment
Description | FL26 to 1600 South
Length of Section | 3.12 mi
Inservice Date | 1966-12-08
Long Seam Type | Unknown
HCA's | 80%
Pop. Dens | LOW to MED
Diameter | 20"
Grade | x42
WT | 0.281
Comments: | HCAs.
Back

## FL42-3 (hidden)
Line | FL42-3
Segment
Description | 1450 West to 200 West
Length of Section | 1.16 mi/6125 ft
Inservice Date | 1966-12-03
Long Seam Type | Unknown
HCA's | 0%
Pop. Dens | MED
Diameter | 6"
Grade | x42
WT | 0.219
Comments: | HCAs and population density.
Back

## FL97 (hidden)
Line | FL97
Segment
Description | Moab
Length of Section | 3.81 mi
Inservice Date | 1963-01-01
Long Seam Type | Unknown
HCA's | 0%
Pop. Dens | LOW
Diameter | 4"
Grade | A24
WT | 0.154
Comments: | SMEs (Utah Gas line) and Lack of pressure test data.
Back

## FL110 (hidden)
Line | FL110
Segment
Description | Vernal
Length of Section | 42 mi
Inservice Date | 1974-02-18
Long Seam Type | ERW
HCA's | 0%
Pop. Dens | LOW
Diameter | 8"
Grade | x42
WT | 0.188
Comments: | SMEs (Utah Gas line)
Back

## FL89 (hidden)
Line | FL89
Segment
Description | Vernal
Length of Section | 3.71 mi
Inservice Date | 1956-02-21
Long Seam Type | Continuous
HCA's | 0%
Pop. Dens | LOW
Diameter | 4"
Grade | B
WT | 0.188
Comments: | SMEs (Utah Gas line)
Back

## FL98 (hidden)
Line | FL98
Segment
Description | Monticello
Length of Section | 12 mi
Inservice Date | 1956-02-21
Long Seam Type | Continuous
HCA's | 0%
Pop. Dens | LOW
Diameter | 4"
Grade | B
WT | 0.188
Comments: | SMEs (Utah Gas line)
Back