## Appendix A
STRAW MAN Model as presented to Technical Workshop in Meeting Notice on April 19, 2011- R746-313. Electrical Service Reliability | PROPOSED Rules January 12, 2012 version - R746-313. Electrical Service Reliability | PROPOSED - R746-313. Electrical Service Reliability As Filed on 5/15/2012 in DAR FILE NO. 36214 | Rocky Mountain Power PROPOSED 6/2012 - R746-313. Electrical Service Reliability
Rule 746-313-1. Authority. | Rule 746-312-1. Authority. | Rule 746-313-1. Authority. | Rule 746-313-1. Authority.
(1) This rule establishes electric service reliability and continuity requirements as provided for in Sections 54-3-2, 54-4-2 and 54-4-7. | (1) This rule establishes electric service reliability and continuity requirements as provided for in Sections 54-3-2, 54-4-2 and 54-4-7. | (1) This rule establishes electric service reliability and continuity requirements as provided for in Utah Code Sections 54-3-1, 54-4-2 and 54-4-7. | (1) This rule establishes electric service reliability and continuity requirements as provided for in Utah Code Sections 54-3-1, 54-4-2 and 54-4-7.
R746-313-2. Definitions | Rule 746-313-2. Definitions. | Rule 746-313-2. Definitions. | Rule 746-313-2. Definitions.
(1) “Electric corporation” means an electric public utility, as defined in Utah Code 54-2-(16). | (1) “CAIDI” means customer average interruption duration index. | (1) “Customer average interruption duration index” (“CAIDI”) has the same meaning as in IEEE 1366 or RUS 1730A-119, as applicable. | (1) “Customer average interruption duration index” (“CAIDI”) has the same meaning as in IEEE 1366 or RUS 1730A-119, as applicable.
(2) “Governing Authority” means | (2) “Electric company” means a public utility, as defined in Utah Code 54-2-(16), that supplies electricity. | (2) “Customer” means, when used for reliability indices calculations, a metered electrical service point for which an active bill account is established at a specific location. | (2) “Customer” means, when used for reliability indices calculations, a metered electrical service point for which an active bill account is established at a specific location where interruption data is collected.
(a) for a distribution electric cooperative, its board of directors; and | (3) “Governing Authority” means | (3) “Day” means a 24-hour period beginning at midnight. | (3) “Day” means a 24-hour period; when calculating major event thresholds, it is considered to begin at midnight, while when evaluating interruption events it is not required to begin at midnight.
(b) for each other electrical corporation, the Public Service Commission, otherwise referred to as the commission. | (a) for a distribution electric cooperative, its board of directors; and | (4) “Electric company” means an electrical corporation or a distribution electrical cooperative that is also a public utility, as defined in Utah Code 54-2-1(16). | (4) “Electric company” means an electrical corporation or a distribution electrical cooperative that is also a public utility, as defined in Utah Code 54-2-1(16).
(3) “Interruption duration” means the period (measured in seconds, minutes, or hours) from the initiation of an interruption to a metering point until service has been restored to that metering point. | (b) for each other electrical corporation, the Public Service Commission of Utah, otherwise referred to as the commission. | (5) “Form 7 – Information on Service Interruptions” means: | (5) “Form 7 – Information on Service Interruptions” means:
(4) “Interruption, momentary” means a single interruption with a duration of five minutes or less. | (4) “IEEE 1366” means the Institute of Electrical Electronic Engineers (IEEE) Standard 1366-2003 entitled “IEEE Guide for Electric Power Distribution Reliability Indices.” | (a) Part G of the United States Department of Agriculture Rural Utilities Service Form 7 Financial and Statistical Report, | (a) Part G of the United States Department of Agriculture Rural Utilities Service Form 7 Financial and Statistical Report,
(5) “Interruption event, momentary” means: | (5) “Interruption” means the loss of service to one or more customers connected to the distribution portion of the system. It is the result of one or more component outages, depending on system configuration. | (b) Part H of the National Rural Utilities Cooperative Finance Corporation Form 7 Financial and Statistical Report, or | (b) Part H of the National Rural Utilities Cooperative Finance Corporation Form 7 Financial and Statistical Report, or
(a) A momentary interruption; or | (6) “Loss of Supply – Substation” or “Power Supply – Substation” means an interruption cause category related to an outage of a distribution substation component. | (c) their equivalents. | (c) their equivalents.
(b) A series of momentary interruptions that is restored by an automatic interruption device, is limited to a single relay sequence, and does not exceed five minutes, such as when an auto-reclose breaker operates two or more times in a single relay sequence and then holds. | (7) “Loss of Supply – Transmission” or “Power Supply – Transmission” means an interruption cause category related to the interruption of the electrical supply by the electric company’s transmission system or by another electrical utility or operator. | (6) “Governing Authority” means: | (6) “Governing Authority” means:
(6) “Interruption, sustained” means an interruption with a duration of greater than five minutes. | (8) "MAIFI(E)" means momentary average interruption event frequency index. (Note -This index does not include events immediately preceding a lockout.) | (a) for a distribution electrical cooperative as defined in Utah Code 54-2-1(6), its board of directors; and | (a) for a distribution electrical cooperative as defined in Utah Code 54-2-1(6), its board of directors; and
(7) “Interruption” means the loss of service to one or more metering points. | (9) “Major Event” means a designation given to an event that exceeds the reasonable design and or operational limits of the electric power system. A major event includes at least one Major Event Day (MED). | (b) for an electrical corporation as defined in Utah Code 54-2-1(7), the Public Service Commission of Utah, otherwise referred to as the commission. | (b) for an electrical corporation as defined in Utah Code 54-2-1(7), the Public Service Commission of Utah, otherwise referred to as the commission.
(8) “Loss of service” means a complete loss of voltage to one or more metering points, but does not include power quality issues such as transients, sags, swells, flickers, harmonics, and other waveform distortions. | (10) “Major Event Day” or “MED” means a day in which the daily system SAIDI exceeds a threshold value, TMED. | (7) “The Institute of Electrical and Electronics Engineers Standard 1366” (“IEEE 1366”) means the 2003 edition of the IEEE Guide for Electric Power Distribution Reliability Indices. | (7) “The Institute of Electrical and Electronics Engineers Standard 1366” (“IEEE 1366”) means the 201203 edition of the IEEE Guide for Electric Power Distribution Reliability Indices.
(9) “MAIFI” means momentary average interruption frequency index. This index is the number of times that a metering point experiences momentary interruption events during a year. It is determined by dividing the total annual number of metering point momentary interruption events by the total number of metering points. Note that this index does not include the events immediately preceding a sustained interruption. | (11) “Operating area” means a geographic subdivision of an electric company's Utah service territory that functions under the direction of an electric company office and as a separate entity used for reliability reporting within the electric company. These areas may also be referred to as regions, divisions, or districts. | (8) “Interruption” means the loss of electrical service to one or more customers connected to the distribution portion of the system. It is the result of one or more component outages, depending on system configuration. | (8) “Interruption” means the loss of electrical service to one or more customers connected to the distribution portion of the system. It is the result of one or more component outages, depending on system configuration.
(10) “Major event” means a catastrophic event that: | (12) “Reliability” means the degree to which electric service is supplied without interruptions. | (9) “Loss of power supply” | (9) “Loss of power supply”
(a) Exceeds the design limits of the electric power system; | (13) “Reliability reporting area” means a grouping of one or more operating areas, for which the electric company calculates major event thresholds. | (a) “Loss of power supply – Distribution Substation” means the loss of the electrical power supply system due to an outage/failure of a distribution substation component. | (a) “Loss of power supply – Distribution Substation” means the loss of the electrical power supply system due to an outage/failure of a distribution substation component.
(b) Causes extensive damage to the electric power system; and | (14) “Reporting Period” means the 12-month period, based on a calendar year, for which an electric company is reporting reliability performance. | (b) “Loss of power supply – Generation/Transmission” means the loss of the electrical power supply from the electric company’s own electric generator or transmission system, including transmission lines and transmission substations, or from another electric company or electric corporation. | (b) “Loss of power supply – Generation/Transmission” means the loss of the electrical power supply from the electric company’s own electric generator or transmission system, including transmission lines and transmission substations, or from another electric company or electric corporation.
(c) Results in a simultaneous sustained interruption to more than 10 percent of the metering points in an operating area. | (15) "RUS 1730A-119" means the United Stated Department of Agriculture Rural Utilities Service Bulletin 1730A-119 entitled "Interruption Reporting and Service Continuity Objectives for Electric Distribution Systems," dated March 24, 2009. | (10) “Momentary average interruption frequency index” (“MAIFI”) has the same meaning as in IEEE 1366 or RUS 1730A-119, as applicable. | (10) “Momentary average interruption frequency index” (“MAIFI”) Momentary interruption has the same meaning as in IEEE 1366 or RUS 1730A-119, as applicable.
(11) “Metering point” means an electric point of service to a customer where there is a meter and for which an electric company renders a bill. | (16) “SAIDI" means system average interruption duration index. | (11) “Major Event” means a designation given to an event that exceeds the reasonable design and or operational limits of the electric power system. As applicable to this rule, a major event includes at least one Major Event Day. | (11) “Major Event” means a designation given to an event that exceeds the reasonable design and or operational limits of the electric power system. As applicable to this rule, a major event includes at least one Major Event Day.
(12) “Metering points, total number of” means the number of metering points as of the last day of the calendar year. | (17) “SAIFI" means system average interruption frequency index. | (12) “Major Event Day” or “med” means a day in which the daily system SAIDI exceeds a threshold value, TMED. | (12) “Major Event Day” or “med” means a day 24 hour period in which the daily system SAIDI exceeds a threshold value, TMED.
(13) “Operating area” means a geographic subdivision of an electric company's Utah service territory that functions under the direction of an electric company office and as a separate entity used for reliability reporting. These areas may also be referred to as regions, divisions, or districts. | (18) “Sustained Interruption” means an interruption lasting more than five minutes. | (13) “Major event day identification threshold value” (“TMED”) has the same meaning as in IEEE 1366 or RUS 1730A-119. | (13) “Major event day identification threshold value” (“TMED”) has the same meaning as in IEEE 1366 or RUS 1730A-119.
(14) “Reliability” means the degree that electric service is supplied without interruptions. | (19) "System-wide" means pertaining to and limited to the electric company's customers in Utah. | (14) “Operating area” means a geographic subdivision of an electric company's Utah service territory that functions under the direction of an electric company office and as a separate entity used for reliability reporting within the electric company. An operating area may also be referred to as regions, divisions, or districts and may also be a reliability reporting area. | (14) “Operating area” means a geographic subdivision of an electric company's Utah service territory that functions under the direction of an electric company office and as a separate entity used for reliability reporting within the electric company. An operating area may also be referred to as regions, divisions, or districts and may also be a reliability reporting area.
(15) “SAIDI” means system average interruption duration index. This is the sustained interruption duration time (in hours) that an average metering point experiences during the year. It is determined by dividing the annual sum of all metering point sustained interruption durations by the total number of metering points. | (20) “TMED” means a major event day identification threshold value as specified in IEEE 1366 and RUS 1730A-119. | (15) “Person” means an individual, a corporation, a partnership, an association, a trust, a company or a regulatory agency. | (15) “Person” means an individual, a corporation, a partnership, an association, a trust, a company or a regulatory agency.
(16) “SAIFI” means system average sustained interruption frequency index. This index is the number of times that an average metering point receives sustained interruptions during a year. It is determined by dividing the total annual number of sustained interruptions by the total number of metering points. |  | (16) “Reliability” means the degree to which electric service is supplied without interruptions. | (16) “Reliability” means the degree to which electric service is supplied without interruptions to customers.
(17) “System-wide” means pertaining to and limited to the electric company's metering points in Utah. |  | (17) “Reliability indices” means the electric service interruption indices identified in IEEE 1366 or RUS 1730A-119, as applicable. | (17) “Reliability indices” means the electric service interruption indices identified in IEEE 1366 or RUS 1730A-119, as applicable.
(18) “Threshold” means a performance level, excluding major events, which requires appropriate electric company action. |  | (18) “Reliability program” means a written electric service reliability program approved by the electric company’s governing authority. | (18) “Reliability program” means a written electric service reliability program approved by the electric company’s governing authority.
(19) “Underperforming circuit” means a circuit characterized by substandard performance. A circuit has this designation if it has a SAIDI, SAIFI, or MAIFI index that exceeds its designated threshold level. |  | (19) “Reliability reporting area” means a grouping of one or more operating areas, for which the electric company calculates major event thresholds. | (19) “Reliability reporting area” means a grouping of one or more operating areas, for which the electric company calculates major event thresholds.
|  | (20) “Reporting Period” means the 12-month period, based on the previous 365 days, or 366 days for leap years, for which an electric company is tracking and reporting reliability performance. | (20) “Reporting Period” means the 12-month period, based on the previous 365 days, or 366 days for leap years, for which an electric company is tracking and reporting reliability performance.
|  | (21) “Rules” means the Electric Service Reliability Rules R746-313-1 through 9. | (21) “Rules” means the Electric Service Reliability Rules R746-313-1 through 9.
|  | (22) “RUS 1730A-119” means the United States Department of Agriculture Rural Utilities Service Bulletin 1730A-119 entitled "Interruption Reporting and Service Continuity Objectives for Electric Distribution Systems," dated March 24, 2009. | (22) “RUS 1730A-119” means the United States Department of Agriculture Rural Utilities Service Bulletin 1730A-119 entitled "Interruption Reporting and Service Continuity Objectives for Electric Distribution Systems," dated March 24, 2009.
|  | (23) “System average interruption duration index” (“SAIDI”) has the same meaning as in IEEE 1366 or RUS 1730A-119, as applicable. | (23) “System average interruption duration index” (“SAIDI”) has the same meaning as in IEEE 1366 or RUS 1730A-119, as applicable.
|  | (24) “System average interruption frequency index” (“SAIFI”) has the same meaning as in IEEE 1366 or RUS 1730A-119, as applicable. | (24) “System average interruption frequency index” (“SAIFI”) has the same meaning as in IEEE 1366 or RUS 1730A-119, as applicable.
|  | (25) “Step restoration” means the process of restoring all interrupted customers in stages over time. | (25) “Step restoration” means the process of restoring all interrupted customers in stages over time.
|  | (26) “Sustained interruption” means an interruption lasting more than five minutes. | (26) “Sustained interruption” means an interruption lasting more than five minutes.
|  | (27) “System-wide” means pertaining to and limited to the electric company's customers in Utah. | (27) “System-wide” means pertaining to and limited to the electric company's customers in Utah.
| Rule 746-313-3. Purpose, Scope, Applicability and Exceptions. | Rule 746-313-3. Purpose, Scope, Applicability and Exceptions. | Rule 746-313-3. Purpose, Scope, Applicability and Exceptions.
| (1) This rule establishes requirements for each electric utility to have a program to ensure reliable electric service is provided to each electric service customer in accordance with the requirements of Utah Code 54-3-1. | (1) This rule establishes requirements for each electric company to have a program to ensure reliable electric service is provided to each electric service customer in accordance with the requirements of Utah Code 54-3-1. | (1) This rule establishes requirements for each electric company to have a program to ensure reliable electric service is provided to each electric service customer in accordance with the requirements of Utah Code 54-3-1.
| (2) An electric company whose governing authority is the Commission shall: | (2) An electric company whose governing authority is the commission shall: | (2) An electric company whose governing authority is the commission shall:
| (a) follow the provisions of IEEE 1366 in the collection and analysis of interruption data and in the calculation and reporting of reliability indices as required by these Electric Service Reliability Rules. If there is a conflict between any provision in IEEE 1366 and these Electric Service Reliability Rules, the Electric Service Reliability Rules R746-313-1 through R746-313-9 govern. | (a) follow the provisions of IEEE 1366 in the collection and analysis of interruption data and in the calculation and reporting of reliability indices as required by these rules. If there is a conflict between any provision in IEEE 1366 and the rules, the rules govern; and | (a) follow the provisions of IEEE 1366 in the collection and analysis of interruption data and in the calculation and reporting of reliability indices as required by these rules. If there is a conflict between any provision in IEEE 1366 and the rules, the rules govern; and
| (b) include both “distribution system” interruptions and “interruptions caused by events outside of the distribution system” as defined in IEEE 1366 in the electric company’s record keeping, calculations, reporting, and filing as required by the Electric Service Reliability Rules R746-313-4 through R746-313-9. | (b) include both “distribution system” interruptions and “interruptions caused by events outside of the distribution system,” as defined in IEEE 1366, in the electric company’s record keeping, calculations, reporting, and filing as required by R746-313-4 through R746-313-9. | (b) include both “distribution system” interruptions and “interruptions caused by events outside of the distribution system,” as defined in IEEE 1366, in the electric company’s record keeping, calculations, reporting, and filing as required by R746-313-4 through R746-313-9.
| (3) An electric company whose governing authority is not the Commission shall: | (3) An electric company whose governing authority is not the commission shall: | (3) An electric company whose governing authority is not the commission shall:
| (a) follow the provision of either IEEE 1366 or the Rural Utility Service Bulletin 1730A-119 in the collection and analysis of interruption data and in the calculation and reporting of reliability indices as required by Electric Service Reliability Rules. If there is a conflict between any provision in IEEE 1366 or RUS 1730A-119 and these Electric Service Reliability Rules, the Electric Service Reliability Rules R746-313-1 through R746-313-9 govern. | (a) follow the provisions of either IEEE 1366 or the RUS Bulletin 1730A-119 in the collection and analysis of interruption data and in the calculation and reporting of reliability indices as required by these rules. If a conflict exists between any provision in IEEE 1366 or RUS 1730A-119 and the rules, the rules govern; and | (a) follow the provisions of either IEEE 1366 or the RUS Bulletin 1730A-119 in the collection and analysis of interruption data and in the calculation and reporting of reliability indices as required by these rules. If a conflict exists between any provision in IEEE 1366 or RUS 1730A-119 and the rules, the rules govern; and
| (b) include both “distribution system” interruptions and interruptions caused by events outside of the distribution system in the electric company’s record keeping, calculations, reporting, and filing as required by the Electric Service Reliability Rules R746-313-4 through R746-313-9. | (b) include both “distribution system” interruptions and interruptions caused by events outside of the distribution system in the electric company’s record keeping, calculations, reporting, and filing as required by the Electric Service Reliability Rules R746-313-4 through R746-313-9. | (b) include both “distribution system” interruptions and interruptions caused by events outside of the distribution system in the electric company’s record keeping, calculations, reporting, and filing as required by the Electric Service Reliability Rules R746-313-4 through R746-313-9.
| (4) Upon written request and for good cause shown, the commission may waive or modify any provision of these Electric Service Reliability Rules in accordance with R746-100-15, Deviation from Rules. | (4) The commission may, upon written request and for good cause shown, waive or modify any provision of these rules in accordance with R746-100-15, Deviation from Rules. | (4) The commission may, upon written request and for good cause shown, waive or modify any provision of these rules in accordance with R746-100-15, Deviation from Rules.
R746-313-3. Electric Service Continuity | Rule 746-313-4. Electric Service Reliability | Rule 746-313-4. Electric Service Reliability Program | Rule 746-313-4. Electric Service Reliability Program
(1) An electric company shall use reasonable means in design, operations, and maintenance to ensure reliable service to each customer. Such means shall include, but not be limited to, programs to prevent service interruptions. | (1) An electric company must use reasonable means in design, operations, and maintenance to ensure reliable service to each customer. Such means include, but are not be limited to, programs to minimize service interruptions. | (1) An electric company must use reasonable means in design, operations, and maintenance to ensure the reliability of electric service provided to each customer in accordance with Utah Code 54-3-1. Such means include, but are not be limited to, programs to minimize service interruptions. | (1) An electric company must use reasonable means in design, operations, and maintenance to ensure the reliability of electric service provided to each customer in accordance with Utah Code 54-3-1. Such means include, but are not be limited to, programs to minimize service interruptions.
(2) By December 31, 2011, an electric company shall have a written electric service reliability/continuity program: | (2) When an interruption occurs, an electric company must reestablish service in a manner which minimizes the interruption duration consistent with the safety of its employees, customers, and the public. | (2) When an interruption occurs, an electric company must reestablish service in a manner which minimizes the interruption duration consistent with the safety of its employees, its customers, and the public. | (2) When an interruption occurs, an electric company must reestablish service in a manner which minimizes the interruption duration consistent with the safety of its employees, its customers, and the public.
(a) approved by its governing authority; | (3) An electric company must have recordkeeping systems in place to determine, and track interruptions, facilitate interruption restoration, and collect and analyze interruption data. | (3) An electric company must have recordkeeping systems in place to determine, and track interruptions, facilitate interruption restoration, and collect and analyze interruption data. | (3) An electric company must have recordkeeping systems in place to determine, and track interruptions, facilitate interruption restoration, and collect and analyze interruption data.
(b) addressing performance measures, goals, and investments necessary for maintaining and/or achieving appropriate electric service and reliability; and | (4) By XXXX, 2012, an electric company whose governing authority is not the Commission shall have a written electric service reliability/continuity program, approved by its governing authority, to ensure service reliability to each customer and to minimize service interruptions. | (4) By December 31, 2012, an electric company whose governing authority is not the commission shall have a written electric service reliability program, approved by its governing authority, to ensure service reliability to each customer and to minimize service interruptions. | (4) By December 31, 2012, an electric company whose governing authority is not the commission shall have a written electric service reliability program, approved by its governing authority, to ensure service reliability to each customer and to minimize service interruptions.
(c) for an electric company whose governing authority is the commission, the written program shall also address vegetation management, maintenance and capital spending, and customer guarantees. | (5) XXX, 2012, an electric company whose governing authority is the Commission shall have a written electric service reliability/continuity program approved by the Commission to ensure service reliability to each customer and to minimize service interruption. | (5) By November 1, 2012, an electric company whose governing authority is the commission shall file a written electric service reliability program for approval by the commission. | (5) Within 6 months of the effective date of this orderBy November 1, 2012, an electric company whose governing authority is the commission shall file a written electric service reliability program for approval by the commission.
(3) When interruptions occur, each electric company shall reestablish service with the shortest possible delay consistent with the safety of its employees, customers, and the general public. | (a) The program shall: | (a) The reliability program must: | (a) The reliability program must:
(4) An electric company shall have a program for analyzing, and where appropriate, for correcting underperforming circuits. | (i) include performance metrics, goals, customer guarantees and other benchmark performance levels necessary for maintaining and/or achieving appropriate electric service and reliability; | (i) be based upon an evaluation of historic electric service reliability information and reliability indices, and service quality commitments; and | identify a reporting plan including deadlines for filed reports as well as plan details which include; 1)reliability results delivered using accepted metrics, 2)identify areas whose performance warrants additional improvement efforts, 3) make provisions for reporting on major events experienced, 4)evaluate interruption events using cause categories as specified in 746-313-8(2)(d)(i)-(xiii). The reporting plan will outline the company's internal processes to collect, monitor and analyze interruption events. The reporting plan will identify the company's service area.
| (ii) be based upon an evaluation of historic electric service reliability information and commitments; | (ii) include both reliability program components as specified in R746-313-4(5)(b) and reliability program supporting information as specified in R746-313-4(5)(d). | (ii) include both reliability program components as specified in R746-313-4(5)(b) and reliability program supporting information as specified in R746-313-4(5)(d).
| (iii) includes methods for identification and correction of worst performing circuits; | (b) Reliability program components are those items and associated programs which establish the levels of electric service reliability to be achieved by the public utility. Reliability program components include but are not limited to: | (b) Reliability program components are those items and associated programs which establish the levels of electric service reliability to be achieved by the public utility. Reliability program components include but are not limited to:
| (iv) include an explanation of efforts supporting the achievement of performance metrics, goals, guarantee levels and benchmarks (e.g., vegetation management and maintenance targets); and | (i) Service reliability performance objectives in the form of network reliability indices, customer guarantees, commitments, and the public utility’s programs necessary for maintaining and/or achieving appropriate electric service and reliability (e.g., vegetation management program, improvement of worst performing circuits program, preventive maintenance programs); | (i) Service reliability performance objectives in the form of network reliability indices, customer guarantees, commitments, and the public utility’s programs necessary for maintaining and/or achieving appropriate electric service and reliability (e.g., vegetation management program, improvement of worst performing circuits program, preventive maintenance programs);
| (v) and include reporting requirements, formats, and schedules. | (ii) identification and description of the electric company’s internal processes, procedures, and/or efforts which support the achievement of performance objectives (e.g., vegetation management, capital investment, and maintenance spending targets; maintenance procedures and schedules; other such programs); | (ii) identification and description of the electric company’s internal processes, procedures, and/or efforts which support the achievement of performance objectives (e.g., vegetation management, capital investment, and maintenance spending targets; maintenance procedures and schedules; other such programs);
| (b) The program shall address how the electric company will comply with the requirements of this rule; | (iii) a plan of action to be implemented and penalties to be assessed in the event a service reliability performance objective or commitment is not met or achieved; | (iii) a plan of action to be implemented and penalties to be assessed in the event a service reliability performance objective or commitment is not met or achieved;
| (c) The program shall explain how the electric company will analyze, and where appropriate, correct underperforming circuits; and | (iv) reporting and meeting commitments and schedules (e.g., semi-annual reports filed with the commission within 120 days after the end of the reporting period, meetings to discuss draft report with the commission within 90 days after the end of the reporting period with draft report to be provided to the commission 10 days before meeting, notification to the commission within 30 days of exceeding any reliability indices or commitments); | (iv) reporting and meeting commitments and schedules (e.g., semi-annual reports filed with the commission within 120 days after the end of the reporting period, meetings to discuss draft report with the commission within 90 days after the end of the reporting period with draft report to be provided to the commission 10 days before meeting, notification to the commission within 30 days of exceeding any reliability indices or commitments);
| (d) The program may also address other issues as an electric company determines appropriate. | (v) a commitment by the electric company to discuss during a scheduled meeting: | (v) a commitment by the electric company to discuss during a scheduled meeting:
| (e) The program may be modified at the request of the electric company. All modifications must be approved prior to implementation and all requests to modify or terminate elements of the program must be accompanied by an evaluation demonstrating the program modifications are reasonable. | (A) reporting period reliability performance, including the results of benchmarking studies in which the public utility has participated; | (A) reporting period reliability performance, including the results of benchmarking studies in which the public utility has participated;
|  | (B) changes to the reliability program components or supporting information; and | (B) changes to the reliability program components or supporting information; and
|  | (C) other relevant electric service reliability topics as appropriate. | (C) other relevant electric service reliability topics as appropriate.
|  | (vi) other commitments and/or program components an electric company determines appropriate. | (vi) other commitments and/or program components an electric company determines appropriate.
|  | (c) Modifications to reliability program components. All modifications to reliability program components must be approved by the commission prior to implementation. | (c) Modifications to reliability program components. All modifications to reliability program components must be approved by the commission prior to implementation.
|  | (d) Reliability program supporting information consists of policies, procedures, methods, systems, and budgets which support the public utility’s reliability program components. Reliability program supporting information includes but is not limited to: | (d) Reliability program supporting information consists of policies, procedures, methods, systems, and budgets which support the public utility’s reliability program components. Reliability program supporting information includes but is not limited to:
|  | (i) an explanation of the process or processes by which the electric company identifies and, where appropriate, corrects underperforming circuits or local areas of performance concerns; | (i) an explanation of the process or processes by which the electric company identifies and, where appropriate, corrects underperforming circuits or local areas of performance concerns;
|  | (ii) general reporting formats and definitions of terms not addressed by these rules or IEEE 1366; | (ii) general reporting formats and definitions of terms not addressed by these rules or IEEE 1366;
|  | (iii) an explanation of how the electric company collects, maintains and verifies the data and determines the specific values used in the calculation of the reliability indices; | (iii) an explanation of how the electric company collects, maintains and verifies the data and determines the specific values used in the calculation of the reliability indices;
|  | (iv) the method for determining the customer count as defined in IEEE 1366; and | (iv) the method for determining the customer count as defined in IEEE 1366; and
|  | (v) other information an electric company determines appropriate. | (v) other information an electric company determines appropriate.
|  | (e) Modifications to reliability program supporting information. An electric company must notify the Commission in writing of any modification to its reliability program supporting information identified in R746-313-4(5)(d) which would affect the consistency of the data being reported under the provisions of the rule at the next scheduled reporting period. The notification must explain the change, the reason for the change, and the effect the change will have on the data. All other modifications to reliability program supporting information must be reported in the electric service reliability report required in R746-313-8. | (e) Modifications to reliability program supporting information. An electric company must notify the Commission in writing of any modification to its reliability program supporting information identified in R746-313-4(5)(d) which would affect the consistency of the data being reported under the provisions of the rule at the next scheduled reporting period. The notification must explain the change, the reason for the change, and the effect the change will have on the data. All other modifications to reliability program supporting information must be reported in the electric service reliability report required in R746-313-8.
|  | (f) All reliability indices identified in the electric company’s reliability program shall be: | (f) All reliability indices identified in the electric company’s reliability program shall be:
|  | (i) calculated with all interruptions included and separately with major event interruptions excluded; | (i) calculated with all interruptions included and separately with major event interruptions excluded;
|  | (ii) based upon and calculated on a 365-day rolling average (or 366-day in the event of a leap year); | (ii) based upon and calculated on a 365-day rolling average (or 366-day in the event of a leap year);
|  | (iii) reported on a system-wide basis and for each reliability reporting area, with the exception that associated circuit- and TMED-related data shall be provided upon request. | (iii) reported on a system-wide basis and for each reliability reporting area, with the exception that associated circuit- and TMED-related data shall be provided upon request.
R746-313-4. Electric Interruption Records | Rule 746-313-5. Electric Service Interruption Records | Rule 746-313-5. Electric Service Interruption Records | Rule 746-313-5. Electric Service Interruption Records
(1) Except as provided in subsection (3) of this section, an electric company shall keep an accurate record of each interruption of service that affects one or more customers. Each record shall contain at least the following information: | (1) Except as provided in subsection (3) of this Section, an electric company using manual methods for tracking reliability shall keep an accurate record of each sustained interruption of service that affects one or more customers. An electric company using automated methods for tracking outages shall keep an accurate record of each interruption of service that affects one or more customers. Each record shall contain at least the following information: | (1) Except as provided in subsection (3) of this Section: | (1) Except as provided in subsection (3) of this Section:
(a) The operating area where the interruption occurred; | (a) The operating area where the interruption occurred; | (a) An electric company using predominantly non-automated methods for identifying outages and tracking reliability shall keep an accurate record of each sustained interruption of service that affects one or more customers. | (a) An electric company using predominantly non-automated methods for identifying outages and tracking reliability shall keep an accurate record of each sustained interruption of service that affects one or more customers.
(b) The name of the substation involved; | (b) The reference identification of the substation involved; | (b) An electric company using an electronic outage management system for identifying electric service interruptions and/or tracking outages shall keep an accurate record of each interruption of service that affects one or more customers. | (b) An electric company using an electronic outage management system for identifying electric service interruptions and/or tracking outages shall keep an accurate record of each interruption of service that affects one or more customers.
(c) The name of the circuit involved; | (c) The reference identification of the circuit involved; | (2) Each record shall contain at least the following information: | (2) Each record shall contain at least the following information:
(d) The date and time the interruption occurred (if the exact time is unknown, the beginning of an interruption is recorded as the earlier of an automatic alarm or the reported initiation time); | (d) The date and time the interruption started or was reported (if the exact time is unknown, the beginning of an interruption is recorded as the earlier of an automatic alarm or the reported initiation time); | (a) the operating area where the interruption occurred; | (a) the operating area where the interruption occurred;
(e) The date and time service was restored; | (e) The date and time service was restored; | (b) the reference identification of the substation involved; | (b) the reference identification of the substation involved;
(f) The duration of the interruption; | (f) The duration of the interruption; | (c) the reference identification of the circuit involved; | (c) the reference identification of the circuit involved;
(g) The number of metering points affected by the interruption; | (g) The number of metering points affected by the interruption; | (d) the date and time the interruption started or was reported. If the exact time is unknown, the beginning of an interruption is recorded as the earlier of an automatic alarm or the reported initiation time; | (d) the date and time the interruption started or was reported. If the exact time is unknown, the beginning of an interruption is recorded as the earlier of an automatic alarm or the reported initiation time;
(h) The cause of the interruption; | (h) The cause of the interruption; | (e) the date and time service was restored; | (e) the date and time service was restored;
(i) The weather conditions at the time of the interruption; | (i) Whether the interruption was planned or unplanned; | (f) the duration of the interruption; | (f) the duration of the interruption;
(j) Whether the interruption was planned or unplanned; | (k) The protective device that made the interruption; and | (g) the number of metering points affected by the interruption; | (g) the number of metering points affected by the interruption;
(k) The protective device that made the interruption; and | (l) The component involved (e.g., transmission line, substation, overhead primary main, underground primary main, transformer, etc.). | (h) the cause of the interruption; | (h) the cause of the interruption;
(l) The component involved (e.g., transmission line, substation, overhead primary main, underground primary main, transformer, etc.). | (2) For interruptions where customers are not simultaneously restored, an electric company shall keep records that document the step-restoration operations. | (i) whether the interruption was planned or unplanned; | (i) whether the interruption was planned or unplanned;
(2) For interruptions where customers are not simultaneously restored, an electric company shall keep records that document the step-restoration operations. | (3) For major events where an electric company is unable to obtain accurate data, the electric company shall make reasonable estimates. | (j) the interrupting device that made the interruption, if known; and | (j) the interrupting device that made the interruption, if known; and
(3) For major events where an electric company cannot obtain accurate data, the electric company shall make reasonable estimates. | (4) An electric company shall retain the records associated with this rule in accordance with R746-310-10 Preservation of Records. | (k) the component involved (e.g., transmission line, substation, overhead primary main, underground primary main, transformer, etc.). | (k) the component involved (e.g., transmission line, substation, overhead primary main, underground primary main, transformer, etc.).
(4) An electric company shall retain for ten years the records associated with subsections (1) and (2) of this rule. |  | (3) For interruptions where customers are not simultaneously restored, an electric company shall keep records that document the step-restoration operations. | (3) For interruptions where customers are not simultaneously restored, an electric company shall keep records that document the step-restoration operations.
|  | (4) For major events where an electric company is unable to obtain accurate data, the electric company shall make reasonable estimates and explain these estimates in any report filed with its governing authority. | (4) For major events where an electric company is unable to obtain accurate data, the electric company shall make reasonable estimates and explain these estimates in any report filed with its governing authority.
|  | (5) An electric company shall retain the records associated with this rule in accordance with R746-310-10 Preservation of Records. | (5) An electric company shall retain the records associated with this rule in accordance with R746-310-10 Preservation of Records.
R746-313-5. Electric Reliability Calculations | Rule 746-313-6. Electric Service Reliability Calculations | Rule 746-313-6. Electric Service Reliability Calculations | Rule 746-313-6. Electric Service Reliability Calculations
(1) Except as provided in section (3) of this rule, an electric company at year-end shall calculate, at a minimum, SAIDI, SAIFI, and MAIFI indices, with and without major events: | (1) Using records collected per R746-313-5, each electric company must perform annual reliability index calculations required by this rule in conformance with the applicable sections of IEEE 1366 or RUS1730A-119. Each electric company must report the results of the calculations in the company’s annual report as set forth in R746-313-89 and in the company’s major event filings as set forth in R746-313-9. | (1) Using records collected in accordance with R746-313-5, each electric company must perform reliability index calculations required by its reliability program in conformance with IEEE 1366 or RUS1730A-119, as applicable. | (1) Using records collected in accordance with R746-313-5, each electric company must perform reliability index calculations required by its reliability program in conformance with IEEE 1366 or RUS1730A-119, as applicable.
(a) On a system-wide basis; | (2) After December 31 of each year an electric company must calculate the reliability index/indices (e.g., SAIDI, SAIFI, CAIDI, etc.) required by the electric company’s written electric service reliability program, for the previous reporting period. These indices are to be calculated both with all interruptions included and separately with major event interruptions excluded: | (2) Each electric company must report the results of any required reliability index calculations for the reporting period in the electric company’s report on electric service reliability as set forth in R746-313-8, and for each major event in the electric company’s major event filings as set forth in R746-313-9. | (2) Each electric company must report the results of any required reliability index calculations for the reporting period in the electric company’s report on electric service reliability as set forth in R746-313-8, and for each major event in the electric company’s major event filings as set forth in R746-313-9.
(b) For each operating area; and | (a) On a system-wide basis; | (3) Data included in the above calculations shall include all interruptions associated with or related to high voltage components (above 600 volts). | (3) Data included in the above calculations shall may include all interruptions associated with or related to high voltage components (above 600 volts).
(c) For each circuit. | (b) For each reliability reporting area; and
(2) Data included in the above calculations shall include all interruptions associated with or related to high voltage components (above 600 volts). | (c) For each circuit.
(3) For each circuit an electric company shall be required to calculate only indices with major events excluded. | (3) Data included in the above calculations shall include all interruptions associated with or related to high voltage components (above 600 volts).
(4) If an electric company estimates MAIFI, it shall specify the method that it used for making the estimate. | (4) For each circuit an electric company shall be required to calculate only indices with major events excluded.
(5) If an electric company estimates or uses factors in calculating actual CAIDI, SAIDI and/or SAIFI indices in sections (1) or (2) of this rule, the company must summarize the estimation methodologies in the company’s annual report in rule R746-313-8.
R746-313-6. Electric Threshold Levels
(1) An electric company shall establish threshold levels for SAIDI, SAIFI, and MAIFI for system-wide operations, each operating area, and each circuit. The following factors should be used to guide the setting of the levels:
(a) Past reliability information;
(b) Demographic, geographic, and electrical characteristics; and
(c) The relative performance of the circuits to each other.
(2) An electric company whose governing authority is the commission shall file with the commission its threshold values and any revision to the values.
R746-313-7. Customer Inquiries about Electric Reliability | Rule 746-313-7. Inquiries about Electric Service Reliability | Rule 746-313-7. Inquiries about Electric Service Reliability | Rule 746-313-7. Inquiries about Electric Service Reliability
(1) A customer may request a report from an electric company about the service reliability of the circuit supplying the customer's own meter. Within 15 business days, the electric company shall supply the report to the customer at no cost. However, if a customer requests an additional reliability report for the same meter within one year of the date of the first request, the electric company may require a deposit from the customer to recover the cost of the report. The electric company shall return the deposit if the additional report indicates that the circuit has become an underperforming circuit, with major events excluded. | (1) A customer may request a report from an electric company about the electric service reliability provided to the customer's own meter. Within 20 business days, the electric company must supply the report to the customer at no cost. However, if a customer requests an additional reliability report for the same meter within one year of the date of the first request, the electric company may charge the customer to recover the actual cost for the report. | (1) A customer may request a report from its electric company about the reliability of the electric service provided to the customer's own meter which the electric company must provide at no cost within 20 business days of the request. If a customer requests one or more additional reliability reports for the same meter within one year of the date of the first request, the electric company may charge the customer the cost of preparing the report(s). | (1) A customer may request a report from its electric company about the reliability of the electric service provided to the customer's own meter which the electric company must provide at no cost within 20 business days of the request. If a customer requests one or more additional reliability reports for the same meter within one year of the date of the first request, the electric company may charge the customer the cost of preparing the report(s).
(2) The report shall include: | (2) For an electric company whose governing authority is the commission, the report to the customer must include: | (2) For an electric company whose governing authority is the commission, the report to the customer must include: | (2) For an electric company whose governing authority is the commission, the report to the customer must include:
(a) The name of the customer; | (a) The name of the customer; | (a) The name of the customer; | (a) The name of the customer;
(b) The date of the request; | (b) The date of the request; | (b) The date of the request; | (b) The date of the request;
(c) The address where the meter is installed; | (c) The address where the meter is installed; | (c) The address where the meter is installed; | (c) The address where the meter is installed;
(d) The meter number involved; | (d) The meter identification number; | (d) The meter identification number; | (d) The meter identification number;
(e) The circuit involved; and | (e) The general identification of the equipment serving the customer; and | (e) The general identification of the equipment serving the customer; and | (e) The general identification of the equipment serving the customer; and
(f) A chronological listing, covering at least 36 months up to the date of the request, of all interruption data as required by R746-313-4 affecting the customer's meter, stating the beginning time, date, duration, and cause for each interruption. | (f) A chronological listing of interruptions, covering at least the 36 months preceding the date of the request, and all interruption data required by R746-313-54 pertaining to the interruptions. | (f) A chronological listing of interruptions to the customer including all associated interruption data required by R746-313-5.(2) covering at least the 36 months preceding the date of the request, if available. If 36 months of data are not available, the chronological listing must include all available data. | (f) A chronological listing of interruptions to the customer including all associated interruption data required by R746-313-5.(2) covering at least the 36 months preceding the date of the request, if available. If 36 months of data are not available, the chronological listing must include all available data.
| (3) For an electric company whose governing authority is not the commission, the report to the customer must include: | (3) For an electric company whose governing authority is not the commission, the report to the customer must include: | (3) For an electric company whose governing authority is not the commission, the report to the customer must include:
| (a) The name of the customer; | (a) The name of the customer; | (a) The name of the customer;
| (b) The date of the request; | (b) The date of the request; | (b) The date of the request;
| (c) The address where the meter is installed; | (c) The address where the meter is installed; | (c) The address where the meter is installed;
| (d) The meter identification number; | (d) The meter identification number; | (d) The meter identification number;
| (e) The general identification of the equipment serving the customer; and | (e) The general identification of the equipment serving the customer; and | (e) The general identification of the equipment serving the customer; and
| (f) A chronological listing of interruptions, covering the 12 months preceding the date of the request, and all interruption data required by R746-313-5 pertaining to the interruptions. | (f) A chronological listing of interruptions on the feeder serving the customer’s meter including all interruption data required by R746-313-5(3) covering at least the 12 months preceding the date of the request, and. If 12 months of data are not available, the chronological listing must include all available data. | (f) A chronological listing of interruptions on the feeder serving the customer’s meter including all interruption data required by R746-313-5(3) covering at least the 12 months preceding the date of the request, and. If 12 months of data are not available, the chronological listing must include all available data.
| (4) Other than those inquiries specified in R746-131-7(1) through (3), each electric company must have a policy for consistent treatment of all other inquiries about electric reliability. At a minimum: | (4) Other than those inquiries specified in R746-313-7(1) through (3), each electric company must have a written policy in its reliability program for consistent treatment of all other inquiries pertaining to electric reliability. At a minimum, the electric company must provide to the inquiring party, by electronic means, the electric company’s most-recently filed Annual Report on Electric Reliability required by R764-313-8. | (4) Other than those inquiries specified in R746-313-7(1) through (3), each electric company must have a written policy in its reliability program for consistent treatment of all other inquiries pertaining to electric reliability. At a minimum, the electric company must provide to the inquiring party, by electronic means, the electric company’s most-recently filed Annual Report on Electric Reliability required by R764-313-8.
(a) an electric company whose governing authority is the Commission must provide the inquiring party access to an electronic version of the electric company’s most recent annual report required by R764-313-8; and
(b) an electric company whose governing authority is not the Commission must provide the inquiring party the interruption data from the most recent annual report required by R764-313-8.
R746-313-8. Public Inquiries about Electric Reliability
(1) Any person may request from an electric company a report about the service reliability for any circuit. The report shall be supplied to the person within 20 working days. A reasonable fee may be charged for each report.
R746-313-9. Annual Report on Electric Reliability | Rule 746-313-8. Annual Report on Electric Reliability | Rule 746-313-8. Report on Electric Service Reliability | Rule 746-313-8. Report on Electric Service Reliability
(1) On or before April 1 of each year, an electric company whose governing authority is the commission shall file with the commission a report that includes reliability information pertaining to the previous calendar year. The electric company shall make copies available to the public upon request. | (1) On or before May 1 of each year, an electric company must file with the commission a report that includes the information set forth in section (2) of this rule for the reporting period. The electric company must file the report in both paper and electronic form. The electric company must make electronic copies of the report available to the public upon request. For paper copies requested by the public, the electric company may charge a reasonable cost for production of the copy. | (1) By May 1 of each year, an electric company shall file with the commission a report on electric service reliability for the reporting period representing the previous calendar year. The electric company must make electronic copies of the report available to the public upon request and may charge a reasonable cost for requested paper copies. | (1) By May 1 of each year, an electric company shall file with the commission a report on electric service reliability for the reporting period representing the previous calendar year. The electric company must make electronic copies of the report available to the public upon request and may charge a reasonable cost for requested paper copies.
(2) In accordance with sections (3) and (4) of this rule, the report shall contain: | (2) For an electric company whose governing authority is the Commission, the annual Electric Service Reliability Report at a minimum, must contain: | (2) For an electric company whose governing authority is the commission, the report on electric service reliability must contain at a minimum: | (2) For an electric company whose governing authority is the commission, the report on electric service reliability must contain at a minimum:
(a) SAIDI, SAIFI, and MAIFI indices and thresholds compared to the most recent four years, both with and without major events: | (a) The results of the calculated reliability indices required by R746-313-6. The electric company must also report this information on a system-wide basis compared with the previous four years’ performance; and | (a) an executive summary including a summary of the electric service reliability program; | (a) an executive summary including a summary of the electric service reliability program;
(i) On a system-wide basis; and | (b) A summary of the system-wide and reliability reporting area sustained interruption causes compared to the previous four-year performance. Cause categories to be evaluated include: | (b) sections addressing the status of all electric reliability performance objectives and supporting programs identified in the electric company’s reliability program; | (b) sections addressing the status of all electric reliability performance objectives and supporting programs identified in the electric company’s reliability program;
(ii) For each operating area. | (A) Loss of Supply – Transmission; | (c) the calculated reliability indices required by the electric company’s reliability program. At a minimum, the electric company must report this information on a system-wide basis compared with the previous four years’ performance and on an operating area compared with the previous four years’ performance; | (c) the calculated reliability indices required by the electric company’s reliability program. At a minimum, the electric company must report this information on a system-wide basis compared with the previous four years’ performance and on an operating area compared with the previous four years’ performance;
(b) SAIDI, SAIFI, and MAIFI indices and thresholds for each circuit, with major events excluded. | (B) Loss of Supply – Substation; | (d) a summary of the system-wide and reliability reporting area sustained interruption causes compared to the previous four-year performance. At a minimum, outages must be categorized using the following cause categories: | (d) a summary of the system-wide and reliability reporting area sustained interruption causes compared to the previous four-year performance. At a minimum, outages must be categorized using the following cause categories:
(c) A summary of the system-wide interruption causes compared to the previous four-year performance. Categories to be evaluated shall include: | (C) Distribution – Equipment; | (i) Loss of Supply – Generation/Transmission; | (i) Loss of Supply – Generation/Transmission;
(i) Adverse environment; | (D) Distribution – Lightning; | (ii) Loss of Supply – Distribution Substation; | (ii) Loss of Supply – Distribution Substation;
(ii) Adverse weather; | (E) Distribution – Planned; | (iii) Distribution – Environment (e.g., unpreventable contamination, corrosion, airborne deposits, flooding, fire/smoke not related to faults or lightning); | (iii) Distribution – Environment (e.g., unpreventable contamination, corrosion, airborne deposits, flooding, fire/smoke not related to faults or lightning);
(iii) Customer equipment; | (F) Distribution – Public; | (iv) Distribution – Equipment Failure; | (iv) Distribution – Equipment Failure;
(iv) Equipment failure; | (G) Distribution – Vegetation; | (v) Distribution – Lightning; | (v) Distribution – Lightning;
(v) Foreign interference; | (H) Distribution –Weather (other than lightning); | (vi) Distribution – Operational; | (vi) Distribution – Operational;
(vi) Human element; | (I) Distribution –Wildlife; | (vii) Distribution – Planned Outages; | (vii) Distribution – Planned Outages;
(vii) Lightning; | (J) Distribution -- Unknown; and | (viii) Distribution – Public; | (viii) Distribution – Public;
(viii) Loss of supply; | (K) Distribution – Other. | (ix) Distribution – Vegetation; | (ix) Distribution – Vegetation;
(ix) Major events; | (c) A listing of the Major Events experienced during the reporting period; | (x) Distribution –Weather (other than lightning); | (x) Distribution –Weather (other than lightning);
(x) Scheduled outages; | (d) A listing of the TMED values that will be used for each reliability reporting area for the forthcoming annual reporting period compared with the previous four years of TMED values; | (xi) Distribution –Wildlife; | (xi) Distribution –Wildlife;
(xi) Tree contacts; | (e) A summary of the characteristics of the data collection systems and estimation methodologies covered by R746-313-5 for the collection of interruption data, calculation of reliability information, and facilitation of interruption restoration and mitigation; | (xii) Distribution -- Unknown; and | (xii) Distribution -- Unknown; and
(xii) Unknown; and | (f) A summary addressing the changes that the electric company has made or will make in the collection of data and the calculation, estimation, and reporting of reliability information. The electric company must explain why the changes occurred and explain how the change affects the comparison of newer and older information; | (xiii) Distribution – Other. | (xiii) Distribution – Other.
(xiii) Other (if used, the electric company shall be specific as to the cause involved). | (g) A map showing the reliability reporting areas and operating areas; | (e) a listing of the major events experienced during the reporting period and a listing of significant events as defined by the electric company, their cause, and their effect on reliability performance during the reporting period; | (e) a listing of the major events experienced during the reporting period and a listing of significant events as defined by the electric company, their cause, and their effect on reliability performance during the reporting period;
(d) A listing of the major events affecting the electric company as determined in R746-313-10. | (h) A listing of circuits by reliability reporting area and substation, indicating circuit voltage and number of customers connected; | (f) comparisons of planned and achieved maintenance spending, maintenance activities, capital spending, vegetation management spending and vegetation management activities including identification of areas of greatest concern and a table summarizing new electrical connections; | (f) comparisons of planned and achieved maintenance spending, maintenance activities, capital spending, vegetation management spending and vegetation management activities including identification of areas of greatest concern and a table summarizing new electrical connections;
(3) An electric company shall present the SAIDI, SAIFI, and MAIFI indices and thresholds in both a tabular and a graphical format. For the graphical format for circuits, an electric company shall compare the SAIDI, SAIFI, and MAIFI indices for each circuit with other circuits in descending order of performance: | (i) A comparison of the electric company’s reliability performance (i.e., SAIDI, SAIFI, and CAIDI) with comparable electric companies; and | (g) a listing of the TMED values that will be used for each reliability reporting area for the forthcoming annual reporting period. | (g) a listing of the TMED values that will be used for each reliability reporting area for the forthcoming annual reporting period.
(a) On a system-wide basis; and | (j) Any other information required to be filed by the electric company’s approved Electric Service Reliability Program pursuant to R746-313-4. | (h) a summary of the data collection systems and estimation methodologies covered by R746-313-5 for the collection of interruption data, calculation of reliability information, and facilitation of interruption restoration and mitigation; | (h) a summary of the data collection systems and estimation methodologies covered by R746-313-5 for the collection of interruption data, calculation of reliability information, and facilitation of interruption restoration and mitigation;
(b) On an operating-area basis. | (3) For an electric company whose governing authority is not the Commission, the annual Electric Service Reliability Report must contain: | (i) a section addressing changes the electric company has made or will make in the collection of data and the calculation, estimation, and reporting of reliability information. The electric company must explain why the changes occurred and explain how the change affects the comparison of newer and older information; | (i) a section addressing changes the electric company has made or will make in the collection of data and the calculation, estimation, and reporting of reliability information. The electric company must explain why the changes occurred and explain how the change affects the comparison of newer and older information;
(4) For historical information prior to the effective date of this rule, the electric company shall provide the best information available. | (a) The results of the calculated reliability indices required by R746-313-6 as presented in the electric company’s Form 7. | (j) a map showing the reliability reporting areas and/or operating areas; | (j) a map showing the reliability reporting areas and/or operating areas;
|  | (k) a listing of circuits by reliability reporting area and substation, indicating circuit voltage and number of customers connected; | (k) a listing of circuits by reliability reporting area and substation, indicating circuit voltage and number of customers connected;
|  | (l) a list of annual reliability-related goals and/or targets set by the electric company for the reporting period addressed by the annual report and for the calendar year in which the report is being submitted; | (l) a list of annual reliability-related goals and/or targets set by the electric company for the reporting period addressed by the annual report and for the calendar year in which the report is being submitted;
|  | (m) an explanation of any factors used in calculating reliability indices presented in the electric company’s annual report and their justification; | (m) an explanation of any factors used in calculating reliability indices presented in the electric company’s annual report and their justification;
|  | (n) a table showing the number of customers by reliability reporting area and operating area, and an explanation of the method used in determining this number; and | (n) a table showing the number of customers by reliability reporting area and operating area, and an explanation of the method used in determining this number; and
|  | (o) any other information required to be filed by the electric company’s reliability program. | (o) any other information required to be filed by the electric company’s reliability program.
|  | (3) For an electric company whose governing authority is not the commission, the report on electric service reliability must contain, at a minimum: | (3) For an electric company whose governing authority is not the commission, the report on electric service reliability must contain, at a minimum:
|  | (a) The reliability indices listed in Form 7 – Information on Service Interruptions based upon the cause codes listed in RUS1730A-119 ; and | (a) The reliability indices listed in Form 7 – Information on Service Interruptions based upon the cause codes listed in RUS1730A-119 ; and
|  | (b) A summary of any estimation methods and/or an explanation of any factors used in calculating reliability indices presented in the electric company’s report on electric service reliability. | (b) A summary of any estimation methods and/or an explanation of any factors used in calculating reliability indices presented in the electric company’s report on electric service reliability.
R746-313-10. Major Event Filing by Electric Utilities | Rule 746-313-9. Major Event Filing by Electric Utilities | Rule 746-313-9. Major Event Reporting by Electric Utilities | Rule 746-313-9. Major Event Reporting by Electric Utilities
(1) Within 20 business days after a major event, an electric company shall submit a report to the Commission which includes: | (1) For each event which an electric company determines to be a major event for network performance calculations: | (1) Major event reporting for an electric company whose governing authority is the commission. Within 30 business days after the conclusion of each event which an electric company determines satisfies the criteria for major event classification in accordance with IEEE 1366, the electric company shall file a major event report with the commission for its consideration. The major event report must include, at a minimum: | (1) Major event reporting for an electric company whose governing authority is the commission. Within 30 business days after the conclusion of each event which an electric company determines satisfies the criteria for major event classification in accordance with IEEE 1366, the electric company shall file a major event report with the commission for its consideration. The major event report must include, at a minimum:
(a) A description of the event; | (a) an electric company whose governing authority is the commission shall submit a major event report to the commission within 30 business days after the conclusion of the event that includes: | (a) a description of the major event, the interruption causes, and a summary of restoration efforts and factors that affected restoration of service; | (a) a description of the major event, the interruption causes, and a summary of restoration efforts and factors that affected restoration of service;
(b) A discussion of why the electric company considers it to be a major event; | (1) A description of the major event, the interruption causes, and a summary of restoration efforts and factors that impacted restoration of service; | (b) identification of reliability reporting area and geographic area affected; | (b) identification of reliability reporting area and geographic area affected;
(c) The total number of metering points affected, the number of metering points without service at periodic intervals, and the longest service interruption; | (2) The reliability reporting area and geographic area impacted; | (c) the total number of customers affected, and the number of customers without service at periodic intervals; | (c) the total number of customers affected, and the number of customers without service at periodic intervals;
(e) The number of crews assigned to restore service at periodic intervals; | (3) The total number of customers affected, and the number of customers without service at periodic intervals; | (d) the calculated SAIDI, SAIFI, MAIFI and CAIDI impacts (i.e., Event SAIDI, SAIFI, MAIFI, and CAIDI) associated with the major event to customers for each reliability reporting area and system-wide; | (d) the calculated SAIDI, SAIFI, MAIFI and CAIDI impacts (i.e., Event SAIDI, SAIFI, MAIFI, and CAIDI) associated with the major event to customers for each reliability reporting area and system-wide;
(f) The estimated SAIDI and SAIFI impact to metering points on a system-wide and an operating-area basis; | (4) The estimated calculated SAIDI, SAIFI, MAIFI and CAIDI impacts (i.e., Event SAIDI, SAIFI, MAIFI, and CAIDI) associated with the Major Event to customers on a reliability reporting area and a system-wide basis. | (e) restoration of service information including resources used and cost; and | (e) restoration of service information including resources used and cost; and
(g) The damage cost estimates to the electric company's facilities; | (5) Restoration of service information including resources used and cost; and | (f) any other information required to be filed by the electric company as specified in its reliability program. | (f) any other information required to be filed by the electric company as specified in its reliability program.
(h) The reason timely restoration was beyond the electric company's control; and | (6) Any other information required to be filed by the electric company’s approved Electric Service Reliability Program pursuant to R746-313-4. | (2) Major event reporting for electric company whose governing authority is not the commission. Within a timely period after each event which an electric company determines satisfies the criteria for major event classification in accordance with IEEE 1366 or RUS 1730A-119, as applicable, the electric company shall provide a major event analysis to its governing authority. | (2) Major event reporting for electric company whose governing authority is not the commission. Within a timely period after each event which an electric company determines satisfies the criteria for major event classification in accordance with IEEE 1366 or RUS 1730A-119, as applicable, the electric company shall provide a major event analysis to its governing authority.
(i) A listing of circuits that were affected with sustained interruptions lasting more than four hours. | (2) An electric company whose governing authority is the not the commission shall provide major event analyses determined in accordance with RUS 1730A-119 to its governing authority for review.