## Supply vs Demand Chart
|  | Peak | [5 empty] | East Supply (10-Minute) | West Supply (10-Minute) | East Supply (30-Minute) | West Supply (30-Minute) |  |  | Energy
| East Requirement |  |  | West Requirement | [7 empty] | East Requirement |  |  | West Requirement
Year | Spin (10-minute) | Non-spin (10-minute) | Regulation (30-minute) | Spin (10-minute) | Non-spin (10-minute) | Regulation (30-minute) | Year | East Supply (10-Minute) | West Supply (10-Minute) | East Supply (30-Minute) | West Supply (30-Minute) | Requirement: Spin (10-minute) | Requirement: Non-spin (10-minute) | Requirement: Regulation (30-minute) | Requirement: Spin (10-minute) | Requirement: Non-spin (10-minute) | Requirement: Regulation (30-minute)
2017 | 195.3252 | 195.3252 | 387.4054 | 88.312 | 88.312 | 228.9375 | 2017 | 1686.4249 | 755.3541 | 2321.6729 | 1019.3541 | 128.1505 | 128.1505 | 387.4054 | 63.8266 | 63.8266 | 228.9375 | 1171.1207 | 974.5502 | 515.3042 | -219.1961
2018 | 197.1704 | 197.1704 | 387.4054 | 89.1184 | 89.1184 | 228.9375 | 2018 | 1686.4021 | 760.7745 | 2321.6501 | 1024.7745 | 129.5547 | 129.5547 | 387.4054 | 64.3692 | 64.3692 | 228.9375 | 1265.2374 | 967.1724 | 421.1647 | -206.3979
2019 | 197.9432 | 197.9432 | 390.2016 | 90.7368 | 90.7368 | 231.2054 | 2019 | 1636.4225 | 710.4532 | 2221.6705 | 974.4532 | 130.9899 | 130.9899 | 390.2016 | 64.9507 | 64.9507 | 231.2054 | 1224.9155 | 965.6016 | 411.507 | -255.1484
2020 | 200.2112 | 200.2112 | 390.2016 | 91.0812 | 91.0812 | 231.2054 | 2020 | 1636.5047 | 752.6668 | 2221.7527 | 1016.6668 | 132.4902 | 132.4902 | 390.2016 | 65.2464 | 65.2464 | 231.2054 | 1224.5833 | 967.5365 | 411.9214 | -214.8697
2021 | 202.8684 | 202.8684 | 454.4841 | 91.6496 | 91.6496 | 230.2957 | 2021 | 1596.4225 | 734.1979 | 2101.6705 | 998.1979 | 133.6062 | 133.6062 | 454.4841 | 65.5174 | 65.5174 | 230.2957 | 1224.3801 | 969.5525 | 372.0424 | -235.3546
2022 | 205.2204 | 205.2204 | 454.4841 | 92.2572 | 92.2572 | 230.2957 | 2022 | 1596.4225 | 693.8115 | 2101.6705 | 957.8115 | 135.3884 | 135.3884 | 454.4841 | 66.0039 | 66.0039 | 230.2957 | 1225.3219 | 961.2009 | 371.1006 | -267.3894
2023 | 206.948 | 206.948 | 454.4841 | 92.834 | 92.834 | 230.2957 | 2023 | 1596.4225 | 734.9389 | 2101.6705 | 998.9389 | 137.407 | 137.407 | 454.4841 | 66.5197 | 66.5197 | 230.2957 | 1225.2648 | 948.395 | 371.1577 | -213.4561
2024 | 209.0424 | 209.0424 | 454.4841 | 93.4836 | 93.4836 | 230.2957 | 2024 | 1596.5047 | 734.9279 | 2101.7527 | 998.9279 | 139.3027 | 139.3027 | 454.4841 | 67.2145 | 67.2145 | 230.2957 | 1225.0171 | 955.5388 | 371.4876 | -220.611
2025 | 211.6128 | 211.6128 | 454.4841 | 94.1332 | 94.1332 | 230.2957 | 2025 | 1596.4225 | 735.4511 | 2101.6705 | 999.4511 | 140.7463 | 140.7463 | 454.4841 | 67.5645 | 67.5645 | 230.2957 | 1224.4863 | 914.8664 | 371.9363 | -179.4153
2026 | 211.414 | 211.414 | 454.4841 | 94.6568 | 94.6568 | 230.2957 | 2026 | 1596.4225 | 733.552 | 2101.6705 | 997.552 | 140.3694 | 140.3694 | 454.4841 | 67.9786 | 67.9786 | 230.2957 | 1224.3675 | 944.8505 | 372.055 | -211.2984
2027 | 213.3824 | 213.3824 | 454.4841 | 95.2056 | 95.2056 | 230.2957 | 2027 | 1596.4145 | 734.5108 | 2101.6625 | 998.5108 | 141.5403 | 141.5403 | 454.4841 | 68.4081 | 68.4081 | 230.2957 | 1223.8573 | 942.508 | 372.5573 | -207.9971
2028 | 214.9672 | 214.9672 | 390.1443 | 95.7236 | 95.7236 | 231.7437 | 2028 | 1515.8207 | 735.6604 | 2021.0687 | 999.6604 | 143.255 | 143.255 | 390.1443 | 68.9988 | 68.9988 | 231.7437 | 1415.5502 | 939.4555 | 100.2705 | -203.7951
2029 | 217.5236 | 217.5236 | 389.78 | 96.2864 | 96.2864 | 235.102 | 2029 | 1627.7145 | 701.5107 | 2132.9625 | 899.5107 | 144.9548 | 144.9548 | 389.78 | 69.299 | 69.299 | 235.102 | 1415.3573 | 938.5148 | 212.3573 | -237.0041
2030 | 219.4948 | 219.4948 | 389.78 | 96.7652 | 96.7652 | 235.102 | 2030 | 1577.7145 | 977.7607 | 2002.9625 | 1175.7607 | 146.3833 | 146.3833 | 389.78 | 69.6509 | 69.6509 | 235.102 | 1415.3561 | 938.8002 | 162.3584 | 38.9605
2031 | 221.9028 | 221.9028 | 397.8819 | 97.216 | 97.216 | 232.7989 | 2031 | 1577.7145 | 978.5107 | 2002.9625 | 1176.5107 | 148.0766 | 148.0766 | 397.8819 | 70.0018 | 70.0018 | 232.7989 | 1414.6518 | 933.7694 | 163.0627 | 44.7413
2032 | 225.3692 | 225.3692 | 396.049 | 97.6304 | 97.6304 | 233.7948 | 2032 | 1577.8207 | 979.6604 | 2003.0687 | 1177.6604 | 150.2525 | 150.2525 | 396.049 | 70.5017 | 70.5017 | 233.7948 | 1659.673 | 944.0434 | -81.8523 | 35.617
2033 | 227.3096 | 227.3096 | 397.9763 | 98.098 | 98.098 | 231.5067 | 2033 | 1815.7145 | 945.5098 | 2178.9625 | 1077.5098 | 151.4848 | 151.4848 | 397.9763 | 70.7023 | 70.7023 | 231.5067 | 1660.5395 | 938.2477 | 155.1751 | 7.2621
2034 | 228.4828 | 228.4828 | 391.6512 | 98.4592 | 98.4592 | 231.476 | 2034 | 1815.7145 | 944.7607 | 2178.9625 | 1076.7607 | 153.2223 | 153.2223 | 391.6512 | 71.0413 | 71.0413 | 231.476 | 2000.7525 | 938.1404 | -185.0379 | 6.6203
2035 | 231.3136 | 231.3136 | 401.2417 | 98.896 | 98.896 | 230.5671 | 2035 | 1815.7145 | 945.5107 | 2178.9625 | 1077.5107 | 155.2497 | 155.2497 | 401.2417 | 71.3853 | 71.3853 | 230.5671 | 2000.1794 | 933.3607 | -184.4649 | 12.15
2036 | 234.57 | 234.57 | 435.8371 | 99.3188 | 99.3188 | 230.493 | 2036 | 1815.8207 | 946.6604 | 2179.0687 | 1078.6604 | 157.2786 | 157.2786 | 435.8371 | 71.89 | 71.89 | 230.493 | 2091.5048 | 938.7945 | -275.6841 | 7.8659
| East | [5 empty] | West

## IRP Resource Reserve Setup
| AS1 | AS2 | AS3 | AS5 |  |  | Year 2017 | Updated
Unit Name | Regulation Up | Regulation Down | Spin | 30 Minute Reserve (BAL-001-2 ) | Non-Spin |  | Notes | No Change
BEAR RIVER RESERVES BEARING UNITS | 0 | 0 | 30 | 30 | Yes | Hydro |  | Hydro
CHEHALIS | 218 | 218 | 218 | 218 | Yes
CHOLLA 4 | 40 | 40 | 40 | 120 | Yes |  | 30 minute reserve 3x spin
CLEARWATER 1 & 2 | 0 | 0 | 0 | 0 | Yes | Hydro
COLSTRIP 3 & 4 | 0 | 0 | 0 | 0 | Yes |  | In Colorado not in company control area, no reserves available
COPCO 1 & 2 | 55 | 0 | 55 | 55 | Yes | Hydro
CRAIG 1 & 2 | 0 | 0 | 0 | 0 | Yes |  | In Colorado not in company control area, no reserves available
CURRANT CREEK | 165 | 165 | 165 | 165 | Yes
CURRANT CREEK (Duct Fire) | 50 | 50 | 50 | 50 | Yes
DAVE JOHNSTON 1 | 11.2 | 11.2 | 11.2 | 11.2 | Yes |  | Transmission limited on 30 minute reserve
DAVE JOHNSTON 2 | 11.2 | 11.2 | 11.2 | 11.2 | Yes |  | Transmission limited on 30 minute reserve
DAVE JOHNSTON 3 | 23.3 | 23.3 | 23.3 | 23.3 | Yes |  | Transmission limited on 30 minute reserve
DAVE JOHNSTON 4 | 35 | 35 | 35 | 35 | Yes |  | Transmission limited on 30 minute reserve
FISH CREEK | 0 | 0 | 0 | 0 | Yes | Hydro
GADSBY 1 | 25 | 25 | 25 | 25 | Yes
GADSBY 2 | 25 | 25 | 25 | 25 | Yes
GADSBY 3 | 38 | 38 | 38 | 70 | Yes |  | 30 minute reserve set 70 MW
GADSBY 4 | 30 | 30 | 30 | 40 | Yes |  | 30 minute reserve full capacity
GADSBY 5 | 30 | 30 | 30 | 40 | Yes |  | 30 minute reserve full capacity
GADSBY 6 | 30 | 30 | 30 | 40 | Yes |  | 30 minute reserve full capacity
HAYDEN 1 & 2 | 0 | 0 | 0 | 0 | Yes |  | In Colorado not in company control area, no reserves available
HERMISTON 1 | 50 | 50 | 50 | 50 | Yes
HERMISTON 2 | 50 | 50 | 50 | 50 | Yes
HUNTER 1 | 37.5 | 37.5 | 37.5 | 112.5 | Yes |  | 30 minute reserve 3x spin
HUNTER 2 | 24.124 | 24.124 | 24.124 | 72.372 | Yes |  | 30 minute reserve 3x spin
HUNTER 3 | 40 | 40 | 40 | 120 | Yes |  | 30 minute reserve 3x spin
HUNTINGTON 1 | 40 | 40 | 40 | 120 | Yes |  | 30 minute reserve 3x spin
HUNTINGTON 2 | 40 | 40 | 40 | 120 | Yes |  | 30 minute reserve 3x spin
JC BOYLE | 0 | 0 | 0 | 0 | Yes | Hydro
JIM BRIDGER 1 | 33 | 33 | 33 | 99 | Yes |  | 30 minute reserve 3x spin
JIM BRIDGER 2 | 33 | 33 | 33 | 99 | Yes |  | 30 minute reserve 3x spin
JIM BRIDGER 3 | 33 | 33 | 33 | 99 | Yes |  | 30 minute reserve 3x spin
JIM BRIDGER 4 | 33 | 33 | 33 | 99 | Yes |  | 30 minute reserve 3x spin
LAKE SIDE | 195 | 195 | 195 | 195 | Yes
LAKE SIDE (Duct Fire) | 41 | 41 | 41 | 41 | Yes
LEMOLO | 0 | 0 | 0 | 0 | Yes | Hydro
MERWIN | 0 | 0 | 0 | 0 | Yes | Hydro
MID-COLUMBIA | 62.7111 | 62.7111 | 62.7111 | 62.7111 | Yes | Hydro
NAUGHTON 1 | 10 | 10 | 10 | 30 | Yes |  | 30 minute reserve 3x spin
NAUGHTON 2 | 30 | 40 | 40 | 100 | Yes |  | 30 minute reserve set 100 MW
NAUGHTON 3 | 50 | 50 | 50 | 100 | Yes |  | 30 minute reserve set 100 MW
SWIFT 1 | 224 | 224 | 224 | 330 | Yes | Hydro | 30 minute reserve includes Swift 1 & 2
TOKETEE-SLIDE | 0 | 0 | 0 | 0 | Yes | Hydro
WYODAK | 35.6 | 35.6 | 35.6 | 35.6 | No |  | Transmission limited on 30 minute reserve
YALE | 170 | 170 | 170 | 170 | Yes | Hydro
LAKESIDE II | 193 | 193 | 193 | 193 | Yes
LAKESIDE II (Duct Fire) | 50 | 50 | 50 | 50 | Yes
Units holding Regulation Up and Regulation Down are also able to contrbute to spin and non-spin reserves
Hydro updates are from Tom Burns 7-14-16. Thermal updates were discussed with Tom Burns 7-27-16 and CCCT reserve provided in e-mail 7-28-16.
Reserves are based on an operation view

## Interruptible Load
| Non-spin | Non-spin | Non-spin | Non-spin |  | Non-spin
| East | East | East | East |  | West
Year | Magcorp | Monsanto | Nucor | Coolkeeper | Total | SCL Stateline
2017 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2018 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2019 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2020 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2021 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2022 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2023 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2024 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2025 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2026 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2027 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2028 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2029 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2030 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2031 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2032 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2033 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2034 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2035 | 108 | 47.5 | 76 | 115 | 346.5 | 10
2036 | 108 | 47.5 | 76 | 115 | 346.5 | 10

## Thermal & Renewables
|  |  | Plant Capacity (100% basis) |  |  |  |  | PacifiCorp Share Capacity (PacifiCorp % basis) |  |  |  |  | General Information | [5 empty] | Source: | \\pacificorp.us\dfs\pdxco\psb1\SHARED\PACDataUpdates\Generation Workgroup\PacifiCorp Capacity\PACMW_Data\Old versions\PACMW_Thermal-2014-08-v1.xls
| Plant / Unit | PacifiCorp Share of Capacity | Net Dependable Capacity | Net Maximum Capacity at Boiler MCR | Net Maximum Summer Capacity (May - Oct) | Net Maximum Winter Capacity (Nov-Apr) | Net Minimum Capacity | Net Dependable Capacity | Net Maximum Capacity at Boiler MCR | Net Maximum Summer Capacity (May - Oct) | Net Maximum Winter Capacity (Nov-Apr) | Net Minimum Capacity | Has AGC Capability | Ramp up rate | Ramp down rate | Spinning Reserve Capability | Calculated Spinning Reserve Capability | 30 Minute
|  | Percent | Megawatts | Megawatts | Megawatts | Megawatts | Megawatts | Megawatts | Megawatts | Megawatts | Megawatts | Megawatts | Yes/No | Megawatts/min | Megawatts/min | Megawatts | 1309.924 | 1945.172 | East Total
East/West | Coal-fueled | [15 empty] | 450 | 714 | West Total
East | Carbon 1 | 100% | 67 | 67.3936 | 67 | 67 | 25 | 67 | 67.3936 | 67 | 67 | 25 | Yes | 1 | 1 | 10 | 0
East | Carbon 2 | 100% | 105 | 105 | 105 | 105 | 45 | 105 | 105 | 105 | 105 | 45 | Yes | 1.5 | 1.5 | 15 | 0
East | Cholla 4 | 100% | 395 | 395 | 395 | 395 | 95 | 395 | 395 | 395 | 395 | 95 | Yes | 4 | 8 | 40 | 40 | 120
East | Colstrip 3 | 10% | 740 | 740 | 740 | 740 | 200 | 74 | 74 | 74 | 74 | 20 | No | Minor share owner | Minor share owner | Minor share owner
East | Colstrip 4 | 10% | 740 | 740 | 740 | 740 | 200 | 74 | 74 | 74 | 74 | 20 | No | Minor share owner | Minor share owner | Minor share owner
East | Craig 1 | 19.28% | 427 | 427 | 427 | 427 | 130 | 82.3256 | 82.3256 | 82.3256 | 82.3256 | 25.064 | Yes | Minor share owner | Minor share owner | Minor share owner
East | Craig 2 | 19.28% | 428 | 428 | 428 | 428 | 130 | 82.5184 | 82.5184 | 82.5184 | 82.5184 | 25.064 | Yes | Minor share owner | Minor share owner | Minor share owner
East | Dave Johnston 1 | 100% | 106 | 106 | 105 | 106 | 55 | 106 | 106 | 105 | 106 | 55 | No | 1.1167 | 3 | 11.1667 | 11.2 | 11.2
East | Dave Johnston 2 | 100% | 106 | 106 | 105 | 106 | 55 | 106 | 106 | 105 | 106 | 55 | No | 1.1167 | 3 | 11.1667 | 11.2 | 11.2
East | Dave Johnston 3 | 100% | 220 | 220 | 220 | 220 | 120 | 220 | 220 | 220 | 220 | 120 | No | 2.3333 | 3 | 23.3333 | 23.3 | 23.3
East | Dave Johnston 4 | 100% | 330 | 330.0048 | 330 | 330 | 180 | 330 | 330.0048 | 330 | 330 | 180 | No | 3.5 | 3 | 35 | 35 | 35
East | Hayden 1 | 24.5% | 184 | 184 | 184 | 184 | 95 | 45.08 | 45.08 | 45.08 | 45.08 | 23.275 | Yes | Minor share owner | Minor share owner | Minor share owner
East | Hayden 2 | 12.6% | 262 | 262 | 262 | 262 | 125 | 33.012 | 33.012 | 33.012 | 33.012 | 15.75 | Yes | Minor share owner | Minor share owner | Minor share owner
East | Hunter 1 | 93.75% | 446 | 449.3798 | 446 | 446 | 180 | 418.125 | 421.2935 | 418.125 | 418.125 | 168.75 | Yes | 4.5694 | 4.5694 | 45.6938 | 37.5 | 112.5
East | Hunter 2 | 60.31% | 446 | 449.3798 | 446 | 446 | 180 | 268.9826 | 271.0209 | 268.9826 | 268.9826 | 108.558 | Yes | 4.5694 | 4.5694 | 45.6938 | 24.124 | 72.372
East | Hunter 3 | 100% | 471 | 471 | 471 | 471 | 220 | 471 | 471 | 471 | 471 | 220 | Yes | 5.5 | 5.5 | 55 | 40 | 120
East | Huntington 1 | 100% | 459 | 459.2 | 459 | 459 | 120 | 459 | 459.2 | 459 | 459 | 120 | Yes | 4 | 4 | 40 | 40 | 120
East | Huntington 2 | 100% | 450 | 454.2418 | 450 | 450 | 120 | 450 | 454.2418 | 450 | 450 | 120 | Yes | 4 | 4 | 40 | 40 | 120
West | Jim Bridger 11 | 66.67% | 531 | 531 | 531 | 531 | 120 | 354 | 354 | 354 | 354 | 80 | Yes | 6/8 | 8 | 80 | 33 | 99
West | Jim Bridger 21 | 66.67% | 527 | 527 | 527 | 527 | 120 | 351.3334 | 351.3334 | 351.3334 | 351.3334 | 80 | Yes | 6/8 | 8 | 80 | 33 | 99
West | Jim Bridger 31 | 66.67% | 523 | 523 | 523 | 523 | 120 | 348.6667 | 348.6667 | 348.6667 | 348.6667 | 80 | Yes | 6/8 | 8 | 80 | 33 | 99
West | Jim Bridger 41 | 66.67% | 530 | 530 | 530 | 530 | 120 | 353.3334 | 353.3334 | 353.3334 | 353.3334 | 80 | Yes | 6/8 | 8 | 80 | 33 | 99
East | Naughton 12 | 100% | 156 | 156 | 156 | 156 | 35 | 156 | 156 | 156 | 156 | 35 | Yes | 1/3 | 3 | 10 | 10 | 30
East | Naughton 2 | 100% | 201 | 201 | 201 | 201 | 50 | 201 | 201 | 201 | 201 | 50 | Yes | 4 | 4 | 40 | 40 | 100
East | Naughton 3 | 100% | 330 | 330 | 330 | 330 | 100 | 330 | 330 | 330 | 330 | 100 | Yes | 5 | 5 | 50 | 50 | 100
East | Wyodak3 | 80% | 335 | 335 | 332 | 339.8 | 180 | 268 | 268 | 265.6 | 271.84 | 144 | Yes | 3.5625 | 6 | 35.625 | 35.6 | 35.6
| Coal-fueled Subtotal |  | 9515 | 9526.5997 | 9510 | 9519.8 | 3120 | 6149.377 | 6159.424 | 6144.977 | 6153.217 | 2090.461
Gas-fueled
West | Camas Co-gen4 | 100% | 14 | Not applicable | 10 | 14 | 10 | 14 | 0 | 10 | 14 | 10 | No | Not dispatchable | Not dispatchable | Not dispatchable
West | Chehalis CC5 | 100% | 518 |  | 476.9728 | 506.203 | 300 | 518 | 0 | 476.9728 | 506.203 | 300 | No | 17.5 | 17.5 | 175 | 218 | 218
East | Currant Creek CC6 | 100% | 445 |  | 421 | 450.8333 | 280 | 445 | 0 | 421 | 450.8333 | 280 | Yes | 14 | 8 | 140 | 215 | 215
East | Currant Creek CC w/DF6 | 100% | 550 |  | 524.1667 | 555.6667 | 465 | 550 | 0 | 524.1667 | 555.6667 | 465 | Yes | 8 | 10 | 80
East | Gadsby 1 | 100% | 64 |  | 64 | 64 | 25 | 64 | 0 | 64 | 64 | 25 | Yes | 2.5 | 2.5 | 25 | 25 | 25
East | Gadsby 2 | 100% | 69 |  | 69 | 69 | 20 | 69 | 0 | 69 | 69 | 20 | Yes | 2.5 | 2.5 | 25 | 25 | 25
East | Gadsby 3 | 100% | 104.5 |  | 104.5 | 104.5 | 25 | 104.5 | 0 | 104.5 | 104.5 | 25 | Yes | 3.8 | 3.8 | 38 | 38 | 70
East | Gadsby 47 | 100% | 40 |  | 39.5758 | 40.7032 | 10 | 40 | 0 | 39.5758 | 40.7032 | 10 | Yes | 14.7 | 14.7 | 30 | 30 | 40
East | Gadsby 57 | 100% | 40 |  | 39.5758 | 40.7032 | 10 | 40 | 0 | 39.5758 | 40.7032 | 10 | Yes | 14.7 | 14.7 | 30 | 30 | 40
East | Gadsby 67 | 100% | 40 |  | 39.5758 | 40.7032 | 10 | 40 | 0 | 39.5758 | 40.7032 | 10 | Yes | 14.7 | 14.7 | 30 | 30 | 40
West | Hermiston 18 | 100% | 237 |  | 230.5 | 240.3333 | 154 | 237 | 0 | 230.5 | 240.3333 | 154 | Yes | 5 | 5 | 50 | 50 | 50
West | Hermiston 28 | 100% | 237 |  | 230.5 | 240.3333 | 154 | 237 | 0 | 230.5 | 240.3333 | 154 | Yes | 5 | 5 | 50 | 50 | 50
East | Lake Side 1 CC9 | 100% | 513 |  | 503.3333 | 518.1667 | 318 | 513 | 0 | 503.3333 | 518.1667 | 318 | Yes | 14 | 14 | 140 | 236 | 236
East | Lake Side 1 CC w/DF9 | 100% | 558 |  | 546.1667 | 562.3333 | 517 | 558 | 0 | 546.1667 | 562.3333 | 517 | Yes | 10 | 10 | 41
East | Lake Side 2 CC9 | 100% | 547 |  | 538.1764 | 561.5309 | 354 | 547 | 0 | 538.1764 | 561.5309 | 354 | Yes | 16 | 16 | 160 | 243 | 243
East | Lake Side 2 CC w/DF9 | 100% | 645 |  | 631.2489 | 656.1624 | 565 | 645 | 0 | 631.2489 | 656.1624 | 565 | Yes | 5 | 5 | 50
| Gas-fueled Subtotal | Corrected | 4621.5 |  | 4468.2924 | 4665.1727 | 3217 | 4621.5 | 0 | 4468.2924 | 4665.1727 | 3217
Renewables
East | Blundell 1 | 100% | 23 |  | 23 | 23 | 4 | 23 | 0 | 23 | 23 | 4 | No | 1.2 | 1.2 | 12 | 0 | 0
East | Blundell 211 | 100% | 10 |  | 8.6667 | 10.8333 | 4 | 10 | 0 | 8.6667 | 10.8333 | 4 | No | 1.8 | 1.8 | 6 | 0 | 0
| Renewables Subtotal |  | 33 |  | 31.6667 | 33.8333 | 8 | 33 | 0 | 31.6667 | 33.8333 | 8
| GRAND TOTAL | Corrected | 14169.5 |  | 14009.9591 | 14218.806 | 6345 | 10803.877 | 6159.424 | 10644.9361 | 10852.223 | 5315.461
NOTES
|  | 1 | Jim Bridger ramp rate on all units is 6 MW/min from 120 MW to 420 MW and 8 MW/min from 420 MW to net dependable capacity (full load). The difference is due to coal mills being placed in service in the 120 MW to 420 MW range.
|  | 2 | Naughton unit 1 ramp rate is 3 MW/min from 80 MW to 140 MW and 1 MW/min from 140 MW to 160 MW. The difference is due to the ID fan operating in the upper load range from 140 MW to 160 MW.
|  | 3 | Wyodak minimum capacity can only be reliably achieved when ambient temperatures are at or above 32 deg F to prevent freezing of the air-cooled condenser.
|  | 4 | Camas Co-Generation Plant is a paper mill facility whose MW capacity depends on the output of paper, causing no difference in the summer and winter ratings. Because it is dependant on the paper mill, this unit cannot be dispatched.
|  | 5 | Chehalis rating is for the 2x1 configuration at the average annual ambient temperature of 52 deg F at that site. The 1x1 configuration rating is half of the 2x1 configuration rating and generally occurs during planned outage and forced outage
events. The ramp rate is for both CT's.
|  | 6 | Currant Creek rating is for the 2x1 configuration at the average annual ambient temperature of 51 deg F at that site, with and without duct firing. The 1x1 configuration rating is half of the 2x1 configuration rating and generally occurs during
planned outage and forced outage events. The ramp rate is for both CT's.
|  | 7 | Gadsby 4-6 rating is for the simple cycle combustion turbine configuration at the compressor inlet temperature of 52 deg F.
|  | 8 | Hermiston rating is for the 2x1 configuration at the average annual ambient temperature of 53 deg F at that site.
|  | 9 | Lake Side 1 and Lake Side 2 rating is for the 2x1 configuration at the average annual ambient temperature of 52 deg F at that site, with and without duct firing. The 1x1 configuration rating is half of the 2x1 configuration rating and generally occurs during planned
outage and forced outage events. The ramp rate is for both CT's.
|  | 10 | Lake Side 1 with power augmentation can only occur at full load conditions and above 55 deg F.
|  | 11 | Blundell 2 was formerly known as Blundell Bottoming Cycle. If necessary, ratings will be adjusted as more performance testing and generation data become available.
GLOSSARY OF TERMS
Net Dependable Capacity: the net maximum MW output a unit or configuration can sustain over a specified period of time when not restricted by ambient conditions or deratings. This unit rating may change only as a result of a new performance
test or permanent unit modifiication and can never be changed due to equipment problems, even if they persist for a lengthy period of time, unless the unit is permanently modified as a result
Net Maximum Capacity at Boiler MCR: the net maximum MW output of the unit or configuration at the maximum continuous rating of the boiler. This value is an emergency rating and is to be used only for a limited period of time.
Net Maximum Summer Capacity (May - Oct): the maximum net MW output for the unit or configuration from May 1st through October 31st based on restrictions due to ambient conditions, if any.
Net Maximum Winter Capacity (Nov - Apr): the maximum net MW output for the unit or configuration from November 1st through April 30th based on improvements due to ambient conditions, if any.
Net Minimum Capacity: the minimum net MW output the unit or configuration can be operated at in a safe and stable mode while maintaining a compliant stack emissions regime.
Has AGC Capability: this yes/no question asks if the unit has Automatic Generation Control, which provides the capability for remote generator output control.
Ramp rate: the rate in MW/min that the generator can ramp from minimum load to net maximum capacity. This rate defines the ability of the unit to follow load after minimum capacity has been reached.
Spinning Reserve Capability: the MW's synchronized to the electrical grid that can respond within 10 minutes to a request, in the event of a unit contingency. This value is calculated as the lesser
of the difference between the maximum and minimum capacities or the ramp rate multiplied by 10 minutes.
|  | Plant Capacity (100% basis) |  |  |  |  | PacifiCorp Share Capacity (PacifiCorp % basis) |  |  |  |  | General Information
Plant / Unit | PacifiCorp Share of Capacity | Net Dependable Capacity | Net Maximum Capacity at Boiler MCR | Net Maximum Summer Capacity (May - Oct) | Net Maximum Winter Capacity (Nov-Apr) | Net Minimum Capacity | Net Dependable Capacity | Net Maximum Capacity at Boiler MCR | Net Maximum Summer Capacity (May - Oct) | Net Maximum Winter Capacity (Nov-Apr) | Net Minimum Capacity | Has AGC Capability | Ramp up rate | Ramp down rate | Spinning Reserve Capability
| Percent | Megawatts | Megawatts | Megawatts | Megawatts | Megawatts | Megawatts | Megawatts | Megawatts | Megawatts | Megawatts | Yes/No | Megawatts/min | Megawatts/min | Megawatts
Coal-fueled
Carbon 1 | 100% | 67 | 67.3936 | 67 | 67 | 25 | 67 | 67.3936 | 67 | 67 | 25 | Yes | 1 | 1 | 10
Carbon 2 | 100% | 105 | 105 | 105 | 105 | 45 | 105 | 105 | 105 | 105 | 45 | Yes | 1.5 | 1.5 | 15
Cholla 4 | 100% | 395 | 395 | 395 | 395 | 95 | 395 | 395 | 395 | 395 | 95 | Yes | 4 | 8 | 40
Colstrip 3 | 10% | 740 | 740 | 740 | 740 | 200 | 74 | 74 | 74 | 74 | 20 | No | Minor share owner | Minor share owner | Minor share owner
Colstrip 4 | 10% | 740 | 740 | 740 | 740 | 200 | 74 | 74 | 74 | 74 | 20 | No | Minor share owner | Minor share owner | Minor share owner
Craig 1 | 19.28% | 427 | 427 | 427 | 427 | 130 | 82.3256 | 82.3256 | 82.3256 | 82.3256 | 25.064 | Yes | Minor share owner | Minor share owner | Minor share owner
Craig 2 | 19.28% | 428 | 428 | 428 | 428 | 130 | 82.5184 | 82.5184 | 82.5184 | 82.5184 | 25.064 | Yes | Minor share owner | Minor share owner | Minor share owner
Dave Johnston 1 | 100% | 106 | 106 | 105 | 106 | 55 | 106 | 106 | 105 | 106 | 55 | No | 1.1167 | 3 | 11.1667
Dave Johnston 2 | 100% | 106 | 106 | 105 | 106 | 55 | 106 | 106 | 105 | 106 | 55 | No | 1.1167 | 3 | 11.1667
Dave Johnston 3 | 100% | 220 | 220 | 220 | 220 | 120 | 220 | 220 | 220 | 220 | 120 | No | 2.3333 | 3 | 23.3333
Dave Johnston 4 | 100% | 330 | 330.0048 | 330 | 330 | 180 | 330 | 330.0048 | 330 | 330 | 180 | No | 3.5 | 3 | 35
Hayden 1 | 24.5% | 184 | 184 | 184 | 184 | 95 | 45.08 | 45.08 | 45.08 | 45.08 | 23.275 | Yes | Minor share owner | Minor share owner | Minor share owner
Hayden 2 | 12.6% | 262 | 262 | 262 | 262 | 125 | 33.012 | 33.012 | 33.012 | 33.012 | 15.75 | Yes | Minor share owner | Minor share owner | Minor share owner
Hunter 1 | 93.75% | 446 | 449.3798 | 446 | 446 | 180 | 418.125 | 421.2935 | 418.125 | 418.125 | 168.75 | Yes | 4.5694 | 4.5694 | 45.6938
Hunter 2 | 60.31% | 446 | 449.3798 | 446 | 446 | 180 | 268.9826 | 271.0209 | 268.9826 | 268.9826 | 108.558 | Yes | 4.5694 | 4.5694 | 45.6938
Hunter 3 | 100% | 471 | 471 | 471 | 471 | 220 | 471 | 471 | 471 | 471 | 220 | Yes | 5.5 | 5.5 | 55
Huntington 1 | 100% | 459 | 459.2 | 459 | 459 | 120 | 459 | 459.2 | 459 | 459 | 120 | Yes | 4 | 4 | 40
Huntington 2 | 100% | 450 | 454.2418 | 450 | 450 | 120 | 450 | 454.2418 | 450 | 450 | 120 | Yes | 4 | 4 | 40
Jim Bridger 11 | 66.67% | 531 | 531 | 531 | 531 | 120 | 354 | 354 | 354 | 354 | 80 | Yes | 6/8 | 8 | 80
Jim Bridger 21 | 66.67% | 527 | 527 | 527 | 527 | 120 | 351.3334 | 351.3334 | 351.3334 | 351.3334 | 80 | Yes | 6/8 | 8 | 80
Jim Bridger 31 | 66.67% | 523 | 523 | 523 | 523 | 120 | 348.6667 | 348.6667 | 348.6667 | 348.6667 | 80 | Yes | 6/8 | 8 | 80
Jim Bridger 41 | 66.67% | 530 | 530 | 530 | 530 | 120 | 353.3334 | 353.3334 | 353.3334 | 353.3334 | 80 | Yes | 6/8 | 8 | 80
Naughton 12 | 100% | 156 | 156 | 156 | 156 | 35 | 156 | 156 | 156 | 156 | 35 | Yes | 1/3 | 3 | 10
Naughton 2 | 100% | 201 | 201 | 201 | 201 | 50 | 201 | 201 | 201 | 201 | 50 | Yes | 4 | 4 | 40
Naughton 3 | 100% | 330 | 330 | 330 | 330 | 100 | 330 | 330 | 330 | 330 | 100 | Yes | 5 | 5 | 50
Wyodak3 | 80% | 335 | 335 | 332 | 339.8 | 180 | 268 | 268 | 265.6 | 271.84 | 144 | Yes | 3.5625 | 6 | 35.625
Coal-fueled Subtotal |  | 9515 | 9526.5997 | 9510 | 9519.8 | 3120 | 6149.377 | 6159.424 | 6144.977 | 6153.217 | 2090.461
Gas-fueled
Camas Co-gen4 | 100% | 14 | Not applicable | 10 | 14 | 10 | 14 | 0 | 10 | 14 | 10 | No | Not dispatchable | Not dispatchable | Not dispatchable
Chehalis CC5 | 100% | 518 |  | 476.9728 | 506.203 | 300 | 518 | 0 | 476.9728 | 506.203 | 300 | No | 17.5 | 17.5 | 175
Currant Creek CC6 | 100% | 445 |  | 421 | 450.8333 | 280 | 445 | 0 | 421 | 450.8333 | 280 | Yes | 14 | 8 | 140
Currant Creek CC w/DF6 | 100% | 550 |  | 524.1667 | 555.6667 | 465 | 550 | 0 | 524.1667 | 555.6667 | 465 | Yes | 8 | 10 | 80
Gadsby 1 | 100% | 64 |  | 64 | 64 | 25 | 64 | 0 | 64 | 64 | 25 | Yes | 2.5 | 2.5 | 25
Gadsby 2 | 100% | 69 |  | 69 | 69 | 20 | 69 | 0 | 69 | 69 | 20 | Yes | 2.5 | 2.5 | 25
Gadsby 3 | 100% | 104.5 |  | 104.5 | 104.5 | 25 | 104.5 | 0 | 104.5 | 104.5 | 25 | Yes | 3.8 | 3.8 | 38
Gadsby 47 | 100% | 40 |  | 39.5758 | 40.7032 | 10 | 40 | 0 | 39.5758 | 40.7032 | 10 | Yes | 14.7 | 14.7 | 30
Gadsby 57 | 100% | 40 |  | 39.5758 | 40.7032 | 10 | 40 | 0 | 39.5758 | 40.7032 | 10 | Yes | 14.7 | 14.7 | 30
Gadsby 67 | 100% | 40 |  | 39.5758 | 40.7032 | 10 | 40 | 0 | 39.5758 | 40.7032 | 10 | Yes | 14.7 | 14.7 | 30
Hermiston 18 | 100% | 237 |  | 230.5 | 240.3333 | 154 | 237 | 0 | 230.5 | 240.3333 | 154 | Yes | 5 | 5 | 50
Hermiston 28 | 100% | 237 |  | 230.5 | 240.3333 | 154 | 237 | 0 | 230.5 | 240.3333 | 154 | Yes | 5 | 5 | 50
Lake Side 1 CC9 | 100% | 513 |  | 503.3333 | 518.1667 | 318 | 513 | 0 | 503.3333 | 518.1667 | 318 | Yes | 14 | 14 | 140
Lake Side 1 CC w/DF9 | 100% | 558 |  | 546.1667 | 562.3333 | 517 | 558 | 0 | 546.1667 | 562.3333 | 517 | Yes | 10 | 10 | 41
Lake Side 2 CC9 | 100% | 547 |  | 538.1764 | 561.5309 | 354 | 547 | 0 | 538.1764 | 561.5309 | 354 | Yes | 16 | 16 | 160
Lake Side 2 CC w/DF9 | 100% | 645 |  | 631.2489 | 656.1624 | 565 | 645 | 0 | 631.2489 | 656.1624 | 565 | Yes | 5 | 5 | 50
Gas-fueled Subtotal |  | 3116.5 |  | 3005.7826 | 3134.6418 | 2265 | 3116.5 | 0 | 3005.7826 | 3134.6418 | 2265
Other
Blundell 1 | 100% | 23 |  | 23 | 23 | 4 | 23 | 0 | 23 | 23 | 4 | No | 1.2 | 1.2 | 12
Blundell 211 | 100% | 10 |  | 8.6667 | 10.8333 | 4 | 10 | 0 | 8.6667 | 10.8333 | 4 | No | 1.8 | 1.8 | 6
Renewables Subtotal |  | 33 |  | 31.6667 | 33.8333 | 8 | 33 | 0 | 31.6667 | 33.8333 | 8
GRAND TOTAL |  | 12664.5 |  | 12547.4493 | 12688.2752 | 5393 | 9298.877 | 6159.424 | 9182.4263 | 9321.6922 | 4363.461
NOTES
| 1 | Jim Bridger ramp rate on all units is 6 MW/min from 120 MW to 420 MW and 8 MW/min from 420 MW to net dependable capacity (full load). The difference is due to coal mills being placed in service in the 120 MW to 420 MW range.
Net Dependable Capacity: the net maximum MW output a unit or configuration can sustain over a specified period of time when not restricted by ambient conditions or deratings. This unit rating may change only as a result of a new performance
test or permanent unit modifiication and can never be changed due to equipment problems, even if they persist for a lengthy period of time, unless the unit is permanently modified as a result
Net Maximum Capacity at Boiler MCR: the net maximum MW output of the unit or configuration at the maximum continuous rating of the boiler. This value is an emergency rating and is to be used only for a limited period of time.
Net Maximum Summer Capacity (May - Oct): the maximum net MW output for the unit or configuration from May 1st through October 31st based on restrictions due to ambient conditions, if any.
Net Maximum Winter Capacity (Nov - Apr): the maximum net MW output for the unit or configuration from November 1st through April 30th based on improvements due to ambient conditions, if any.
Net Minimum Capacity: the minimum net MW output the unit or configuration can be operated at in a safe and stable mode while maintaining a compliant stack emissions regime.
Has AGC Capability: this yes/no question asks if the unit has Automatic Generation Control, which provides the capability for remote generator output control.
Ramp rate: the rate in MW/min that the generator can ramp from minimum load to net maximum capacity. This rate defines the ability of the unit to follow load after minimum capacity has been reached.
Spinning Reserve Capability: the MW's synchronized to the electrical grid that can respond within 10 minutes to a request, in the event of a unit contingency. This value is calculated as the lesser
of the difference between the maximum and minimum capacities or the ramp rate multiplied by 10 minutes.
Note on Q29: p07242: Per Terry Riley's suggestion.

## Resources Reserve Capability
Extracted from EPM Model
New Resources |  |  | Capability Pattern |  |  |  |  | Capability (MW)
EntityID | Entity | Reg Up | Reg Down | Spin | Non-Spin | Non-Spin (30 minute) | Reg Up | Reg Down | Spin
| I_UN_SC_Frm | "=No" | "=No" | "=On.Line" | "=On.Line" | "=On.Line" | 0 | 0 | 112 | 2029 | East
| I_WV_CC_G1 | "=No" | "=No" | "=On.Line" | "=On.Line" | "=On.Line" | 0 | 0 | 262 | 2030 | West
| I_WV_CC_G1D | "=No" | "=No" | "=On.Line" | "=On.Line" | "=On.Line" | 0 | 0 | 15 | 2030 | West
| I_DJ_CC_J1 | "=No" | "=No" | "=On.Line" | "=On.Line" | "=On.Line" | 0 | 0 | 285 | 2033 | East
| I_DJ_CC_J1D | =No | =No | =On.Line | =On.Line | =On.Line | 0 | 0 | 19 | 2033 | East
| I_DJ_SC-FRM | =No | =No | =On.Line | =On.Line | =On.Line | 0 | 0 | 112 | 2033 | East
|  | =No | =No | =On.Line | =On.Line | =On.Line | 0 | 0 | 0
|  | =No | =No | =On.Line | =On.Line | =On.Line | 0 | 0 | 0
|  | =No | =No | =On.Line | =On.Line | =On.Line | 0 | 0 | 0
|  | =No | =No | =On.Line | =On.Line | =On.Line | 0 | 0 | 0
|  | =No | =No | =On.Line | =On.Line | =On.Line | 0 | 0 | 0
|  | =No | =No | =On.Line | =On.Line | =On.Line | 0 | 0 | 0
|  | =No | =No | =On.Line | =On.Line | =On.Line | 0 | 0 | 0
|  | =No | =No | =On.Line | =On.Line | =On.Line | 0 | 0 | 0
|  | =No | =No | =On.Line | =On.Line | =On.Line | 0 | 0 | 0
| Total | [5 empty] | 0 | 0 | 805

## Reserve Requirement-PAR
Preferred Portfolio - |  | FS-GW4
1) East Base Reserve Requirement (MW)
| Spin Ratio (%) | Non-Spin Ratio (%) | Avg Load (aMW) | Reg Up | Reg Down | Spin | Non-Spin | 30 minute
2017 | 2.8 | 2.8 | 4576.8022 | 0 | 0 | 128.1505 | 128.1505 | 387.4054
2018 | 2.8 | 2.8 | 4626.9535 | 0 | 0 | 129.5547 | 129.5547 | 387.4054
2019 | 2.8 | 2.8 | 4678.2091 | 0 | 0 | 130.9899 | 130.9899 | 390.2016
2020 | 2.8 | 2.8 | 4731.7934 | 0 | 0 | 132.4902 | 132.4902 | 390.2016
2021 | 2.8 | 2.8 | 4771.6498 | 0 | 0 | 133.6062 | 133.6062 | 454.4841
2022 | 2.8 | 2.8 | 4835.2994 | 0 | 0 | 135.3884 | 135.3884 | 454.4841
2023 | 2.8 | 2.8 | 4907.3914 | 0 | 0 | 137.407 | 137.407 | 454.4841
2024 | 2.8 | 2.8 | 4975.096 | 0 | 0 | 139.3027 | 139.3027 | 454.4841
2025 | 2.8 | 2.8 | 5026.6525 | 0 | 0 | 140.7463 | 140.7463 | 454.4841
2026 | 2.8 | 2.8 | 5013.1944 | 0 | 0 | 140.3694 | 140.3694 | 454.4841
2027 | 2.8 | 2.8 | 5055.01 | 0 | 0 | 141.5403 | 141.5403 | 454.4841
2028 | 2.8 | 2.8 | 5116.2485 | 0 | 0 | 143.255 | 143.255 | 390.1443
2029 | 2.8 | 2.8 | 5176.9574 | 0 | 0 | 144.9548 | 144.9548 | 389.78
2030 | 2.8 | 2.8 | 5227.9733 | 0 | 0 | 146.3833 | 146.3833 | 389.78
2031 | 2.8 | 2.8 | 5288.4486 | 0 | 0 | 148.0766 | 148.0766 | 397.8819
2032 | 2.8 | 2.8 | 5366.1624 | 0 | 0 | 150.2525 | 150.2525 | 396.049
2033 | 2.8 | 2.8 | 5410.1732 | 0 | 0 | 151.4848 | 151.4848 | 397.9763
2034 | 2.8 | 2.8 | 5472.2247 | 0 | 0 | 153.2223 | 153.2223 | 391.6512
2035 | 2.8 | 2.8 | 5544.6305 | 0 | 0 | 155.2497 | 155.2497 | 401.2417
2036 | 2.8 | 2.8 | 5617.0942 | 0 | 0 | 157.2786 | 157.2786 | 435.8371
1) West Base Reserve Requirement (MW)
| Spin Ratio (%) | Non-Spin Ratio (%) | Avg Load (aMW) | Reg Up | Reg Down | Spin | Non-Spin | 30 minute
2017 | 2.8 | 2.8 | 2279.5197 | 0 | 0 | 63.8266 | 63.8266 | 228.9375
2018 | 2.8 | 2.8 | 2298.9016 | 0 | 0 | 64.3692 | 64.3692 | 228.9375
2019 | 2.8 | 2.8 | 2319.6695 | 0 | 0 | 64.9507 | 64.9507 | 231.2054
2020 | 2.8 | 2.8 | 2330.2285 | 0 | 0 | 65.2464 | 65.2464 | 231.2054
2021 | 2.8 | 2.8 | 2339.908 | 0 | 0 | 65.5174 | 65.5174 | 230.2957
2022 | 2.8 | 2.8 | 2357.283 | 0 | 0 | 66.0039 | 66.0039 | 230.2957
2023 | 2.8 | 2.8 | 2375.7045 | 0 | 0 | 66.5197 | 66.5197 | 230.2957
2024 | 2.8 | 2.8 | 2400.5171 | 0 | 0 | 67.2145 | 67.2145 | 230.2957
2025 | 2.8 | 2.8 | 2413.0185 | 0 | 0 | 67.5645 | 67.5645 | 230.2957
2026 | 2.8 | 2.8 | 2427.8059 | 0 | 0 | 67.9786 | 67.9786 | 230.2957
2027 | 2.8 | 2.8 | 2443.1469 | 0 | 0 | 68.4081 | 68.4081 | 230.2957
2028 | 2.8 | 2.8 | 2464.2416 | 0 | 0 | 68.9988 | 68.9988 | 231.7437
2029 | 2.8 | 2.8 | 2474.9647 | 0 | 0 | 69.299 | 69.299 | 235.102
2030 | 2.8 | 2.8 | 2487.5305 | 0 | 0 | 69.6509 | 69.6509 | 235.102
2031 | 2.8 | 2.8 | 2500.0652 | 0 | 0 | 70.0018 | 70.0018 | 232.7989
2032 | 2.8 | 2.8 | 2517.9191 | 0 | 0 | 70.5017 | 70.5017 | 233.7948
2033 | 2.8 | 2.8 | 2525.0822 | 0 | 0 | 70.7023 | 70.7023 | 231.5067
2034 | 2.8 | 2.8 | 2537.1898 | 0 | 0 | 71.0413 | 71.0413 | 231.476
2035 | 2.8 | 2.8 | 2549.4766 | 0 | 0 | 71.3853 | 71.3853 | 230.5671
2036 | 2.8 | 2.8 | 2567.4986 | 0 | 0 | 71.89 | 71.89 | 230.493

## Reserve Requirement-SO
Preferred Portfolio - |  | FS-GW4
1) East Base Reserve Requirement (MW)
| Spin Ratio (%) | Non-Spin Ratio (%) | Peak Load (MW) | Reg Up | Reg Down | Spin | Non-Spin | 30 minute
2017 | 2.8 | 2.8 | 6975.9 | 0 | 0 | 195.3252 | 195.3252 | 387.4054
2018 | 2.8 | 2.8 | 7041.8 | 0 | 0 | 197.1704 | 197.1704 | 387.4054
2019 | 2.8 | 2.8 | 7069.4 | 0 | 0 | 197.9432 | 197.9432 | 390.2016
2020 | 2.8 | 2.8 | 7150.4 | 0 | 0 | 200.2112 | 200.2112 | 390.2016
2021 | 2.8 | 2.8 | 7245.3 | 0 | 0 | 202.8684 | 202.8684 | 454.4841
2022 | 2.8 | 2.8 | 7329.3 | 0 | 0 | 205.2204 | 205.2204 | 454.4841
2023 | 2.8 | 2.8 | 7391 | 0 | 0 | 206.948 | 206.948 | 454.4841
2024 | 2.8 | 2.8 | 7465.8 | 0 | 0 | 209.0424 | 209.0424 | 454.4841
2025 | 2.8 | 2.8 | 7557.6 | 0 | 0 | 211.6128 | 211.6128 | 454.4841
2026 | 2.8 | 2.8 | 7550.5 | 0 | 0 | 211.414 | 211.414 | 454.4841
2027 | 2.8 | 2.8 | 7620.8 | 0 | 0 | 213.3824 | 213.3824 | 454.4841
2028 | 2.8 | 2.8 | 7677.4 | 0 | 0 | 214.9672 | 214.9672 | 390.1443
2029 | 2.8 | 2.8 | 7768.7 | 0 | 0 | 217.5236 | 217.5236 | 389.78
2030 | 2.8 | 2.8 | 7839.1 | 0 | 0 | 219.4948 | 219.4948 | 389.78
2031 | 2.8 | 2.8 | 7925.1 | 0 | 0 | 221.9028 | 221.9028 | 397.8819
2032 | 2.8 | 2.8 | 8048.9 | 0 | 0 | 225.3692 | 225.3692 | 396.049
2033 | 2.8 | 2.8 | 8118.2 | 0 | 0 | 227.3096 | 227.3096 | 397.9763
2034 | 2.8 | 2.8 | 8160.1 | 0 | 0 | 228.4828 | 228.4828 | 391.6512
2035 | 2.8 | 2.8 | 8261.2 | 0 | 0 | 231.3136 | 231.3136 | 401.2417
2036 | 2.8 | 2.8 | 8377.5 | 0 | 0 | 234.57 | 234.57 | 435.8371
1) West Base Reserve Requirement (MW)
| Spin Ratio (%) | Non-Spin Ratio (%) | Peak Load (MW) | Reg Up | Reg Down | Spin | Non-Spin | 30 minute
2017 | 2.8 | 2.8 | 3154 | 0 | 0 | 88.312 | 88.312 | 228.9375
2018 | 2.8 | 2.8 | 3182.8 | 0 | 0 | 89.1184 | 89.1184 | 228.9375
2019 | 2.8 | 2.8 | 3240.6 | 0 | 0 | 90.7368 | 90.7368 | 231.2054
2020 | 2.8 | 2.8 | 3252.9 | 0 | 0 | 91.0812 | 91.0812 | 231.2054
2021 | 2.8 | 2.8 | 3273.2 | 0 | 0 | 91.6496 | 91.6496 | 230.2957
2022 | 2.8 | 2.8 | 3294.9 | 0 | 0 | 92.2572 | 92.2572 | 230.2957
2023 | 2.8 | 2.8 | 3315.5 | 0 | 0 | 92.834 | 92.834 | 230.2957
2024 | 2.8 | 2.8 | 3338.7 | 0 | 0 | 93.4836 | 93.4836 | 230.2957
2025 | 2.8 | 2.8 | 3361.9 | 0 | 0 | 94.1332 | 94.1332 | 230.2957
2026 | 2.8 | 2.8 | 3380.6 | 0 | 0 | 94.6568 | 94.6568 | 230.2957
2027 | 2.8 | 2.8 | 3400.2 | 0 | 0 | 95.2056 | 95.2056 | 230.2957
2028 | 2.8 | 2.8 | 3418.7 | 0 | 0 | 95.7236 | 95.7236 | 231.7437
2029 | 2.8 | 2.8 | 3438.8 | 0 | 0 | 96.2864 | 96.2864 | 235.102
2030 | 2.8 | 2.8 | 3455.9 | 0 | 0 | 96.7652 | 96.7652 | 235.102
2031 | 2.8 | 2.8 | 3472 | 0 | 0 | 97.216 | 97.216 | 232.7989
2032 | 2.8 | 2.8 | 3486.8 | 0 | 0 | 97.6304 | 97.6304 | 233.7948
2033 | 2.8 | 2.8 | 3503.5 | 0 | 0 | 98.098 | 98.098 | 231.5067
2034 | 2.8 | 2.8 | 3516.4 | 0 | 0 | 98.4592 | 98.4592 | 231.476
2035 | 2.8 | 2.8 | 3532 | 0 | 0 | 98.896 | 98.896 | 230.5671
2036 | 2.8 | 2.8 | 3547.1 | 0 | 0 | 99.3188 | 99.3188 | 230.493

## Reserves Demand Table
Spin & Nonspin: |  | \\pdxfilc21p\par\data1\2017 IRP\1-Document\Appendix F - Flexible Reserve Study\Support\Preferred Portfolio FS-GW4 Reserves inputs worksheet.xlsx
| East Operating Reserves Demand (aMW) |  |  |  | West Operating Reserves Demand (aMW) |  |  |  |  | East Operating Reserves Max Demand (MW) |  |  |  | West Operating Reserves Max Demand (MW)
| SPIN | NONSPIN | 30 Minute | TOTAL | SPIN | NONSPIN | 30 Minute | TOTAL |  | SPIN | NONSPIN | 30 Minute | TOTAL | SPIN | NONSPIN | 30 Minute | TOTAL
2017 | 128.1505 | 128.1505 | 387.4054 | 643.7064 | 63.8266 | 63.8266 | 228.9375 | 356.5906 | 2017 | 195.3252 | 195.3252 | 387.4054 | 778.0558 | 88.312 | 88.312 | 228.9375 | 405.5615
2018 | 129.5547 | 129.5547 | 387.4054 | 646.5148 | 64.3692 | 64.3692 | 228.9375 | 357.676 | 2018 | 197.1704 | 197.1704 | 387.4054 | 781.7462 | 89.1184 | 89.1184 | 228.9375 | 407.1743
2019 | 130.9899 | 130.9899 | 390.2016 | 652.1813 | 64.9507 | 64.9507 | 231.2054 | 361.1069 | 2019 | 197.9432 | 197.9432 | 390.2016 | 786.088 | 90.7368 | 90.7368 | 231.2054 | 412.679
2020 | 132.4902 | 132.4902 | 390.2016 | 655.182 | 65.2464 | 65.2464 | 231.2054 | 361.6982 | 2020 | 200.2112 | 200.2112 | 390.2016 | 790.624 | 91.0812 | 91.0812 | 231.2054 | 413.3678
2021 | 133.6062 | 133.6062 | 454.4841 | 721.6965 | 65.5174 | 65.5174 | 230.2957 | 361.3305 | 2021 | 202.8684 | 202.8684 | 454.4841 | 860.2209 | 91.6496 | 91.6496 | 230.2957 | 413.5949
2022 | 135.3884 | 135.3884 | 454.4841 | 725.2609 | 66.0039 | 66.0039 | 230.2957 | 362.3035 | 2022 | 205.2204 | 205.2204 | 454.4841 | 864.9249 | 92.2572 | 92.2572 | 230.2957 | 414.8101
2023 | 137.407 | 137.407 | 454.4841 | 729.298 | 66.5197 | 66.5197 | 230.2957 | 363.3351 | 2023 | 206.948 | 206.948 | 454.4841 | 868.3801 | 92.834 | 92.834 | 230.2957 | 415.9637
2024 | 139.3027 | 139.3027 | 454.4841 | 733.0895 | 67.2145 | 67.2145 | 230.2957 | 364.7247 | 2024 | 209.0424 | 209.0424 | 454.4841 | 872.5689 | 93.4836 | 93.4836 | 230.2957 | 417.2629
2025 | 140.7463 | 140.7463 | 454.4841 | 735.9767 | 67.5645 | 67.5645 | 230.2957 | 365.4247 | 2025 | 211.6128 | 211.6128 | 454.4841 | 877.7097 | 94.1332 | 94.1332 | 230.2957 | 418.5621
2026 | 140.3694 | 140.3694 | 454.4841 | 735.223 | 67.9786 | 67.9786 | 230.2957 | 366.2528 | 2026 | 211.414 | 211.414 | 454.4841 | 877.3121 | 94.6568 | 94.6568 | 230.2957 | 419.6093
2027 | 141.5403 | 141.5403 | 454.4841 | 737.5647 | 68.4081 | 68.4081 | 230.2957 | 367.1119 | 2027 | 213.3824 | 213.3824 | 454.4841 | 881.2489 | 95.2056 | 95.2056 | 230.2957 | 420.7069
2028 | 143.255 | 143.255 | 390.1443 | 676.6543 | 68.9988 | 68.9988 | 231.7437 | 369.7412 | 2028 | 214.9672 | 214.9672 | 390.1443 | 820.0787 | 95.7236 | 95.7236 | 231.7437 | 423.1909
2029 | 144.9548 | 144.9548 | 389.78 | 679.6896 | 69.299 | 69.299 | 235.102 | 373.7001 | 2029 | 217.5236 | 217.5236 | 389.78 | 824.8272 | 96.2864 | 96.2864 | 235.102 | 427.6748
2030 | 146.3833 | 146.3833 | 389.78 | 682.5465 | 69.6509 | 69.6509 | 235.102 | 374.4037 | 2030 | 219.4948 | 219.4948 | 389.78 | 828.7696 | 96.7652 | 96.7652 | 235.102 | 428.6324
2031 | 148.0766 | 148.0766 | 397.8819 | 694.035 | 70.0018 | 70.0018 | 232.7989 | 372.8025 | 2031 | 221.9028 | 221.9028 | 397.8819 | 841.6875 | 97.216 | 97.216 | 232.7989 | 427.2309
2032 | 150.2525 | 150.2525 | 396.049 | 696.5541 | 70.5017 | 70.5017 | 233.7948 | 374.7982 | 2032 | 225.3692 | 225.3692 | 396.049 | 846.7874 | 97.6304 | 97.6304 | 233.7948 | 429.0556
2033 | 151.4848 | 151.4848 | 397.9763 | 700.9459 | 70.7023 | 70.7023 | 231.5067 | 372.9113 | 2033 | 227.3096 | 227.3096 | 397.9763 | 852.5955 | 98.098 | 98.098 | 231.5067 | 427.7027
2034 | 153.2223 | 153.2223 | 391.6512 | 698.0958 | 71.0413 | 71.0413 | 231.476 | 373.5586 | 2034 | 228.4828 | 228.4828 | 391.6512 | 848.6168 | 98.4592 | 98.4592 | 231.476 | 428.3944
2035 | 155.2497 | 155.2497 | 401.2417 | 711.741 | 71.3853 | 71.3853 | 230.5671 | 373.3378 | 2035 | 231.3136 | 231.3136 | 401.2417 | 863.8689 | 98.896 | 98.896 | 230.5671 | 428.3591
2036 | 157.2786 | 157.2786 | 435.8371 | 750.3944 | 71.89 | 71.89 | 230.493 | 374.2729 | 2036 | 234.57 | 234.57 | 435.8371 | 904.9771 | 99.3188 | 99.3188 | 230.493 | 429.1306

## Reserves Supply Table
| (10-minute) | [6 empty] | (30-minute)
| East and West Operating Reserves Supply (aMW) | [6 empty] | East and West Operating Reserves Supply (aMW)
| East | West | [5 empty] | East | West
| SPIN | SPIN | East |  | West |  |  | SPIN | SPIN
2017 | 1339.9249 | 745.3541 |  |  |  |  | 2017 | 1975.1729 | 1009.3541
2018 | 1339.9021 | 750.7745 |  |  |  |  | 2018 | 1975.1501 | 1014.7745
2019 | 1289.9225 | 700.4532 | NT3 retire |  |  |  | 2019 | 1875.1705 | 964.4532
2020 | 1290.0047 | 742.6668 |  |  |  |  | 2020 | 1875.2527 | 1006.6668
2021 | 1249.9225 | 724.1979 | Cholla Retire |  |  |  | 2021 | 1755.1705 | 988.1979
2022 | 1249.9225 | 683.8115 |  |  |  |  | 2022 | 1755.1705 | 947.8115
2023 | 1249.9225 | 724.9389 |  |  |  |  | 2023 | 1755.1705 | 988.9389
2024 | 1250.0047 | 724.9279 |  |  |  |  | 2024 | 1755.2527 | 988.9279
2025 | 1249.9225 | 725.4511 |  |  |  |  | 2025 | 1755.1705 | 989.4511
2026 | 1249.9225 | 723.552 |  |  |  |  | 2026 | 1755.1705 | 987.552
2027 | 1249.9145 | 724.5108 |  |  |  |  | 2027 | 1755.1625 | 988.5108
2028 | 1169.3207 | 725.6604 | Remove DJ |  |  |  | 2028 | 1674.5687 | 989.6604
2029 | 1281.2145 | 691.5107 | Add FRM |  | Remove JB1 |  | 2029 | 1786.4625 | 889.5107
2030 | 1231.2145 | 967.7607 | Remove Naughton 1,2, |  | Add CT |  | 2030 | 1656.4625 | 1165.7607
2031 | 1231.2145 | 968.5107 |  |  |  |  | 2031 | 1656.4625 | 1166.5107
2032 | 1231.3207 | 969.6604 |  |  |  |  | 2032 | 1656.5687 | 1167.6604
2033 | 1469.2145 | 935.5098 | Add CT & ST, remove Gass |  | Remove JB2 |  | 2033 | 1832.4625 | 1067.5098
2034 | 1469.2145 | 934.7607 |  |  |  |  | 2034 | 1832.4625 | 1066.7607
2035 | 1469.2145 | 935.5107 |  |  |  |  | 2035 | 1832.4625 | 1067.5107
2036 | 1469.3207 | 936.6604 |  |  |  |  | 2036 | 1832.5687 | 1068.6604
10-minute
|  | East Hydro Reserve Capability (aMW) |  |  | RegUp
|  |  |  | Bear River | Small East Hydro | GemState_99489 | Total
|  |  | 2017 | 30.0009 | 0 | 0 | 30.0009
|  |  | 2018 | 29.9781 | 0 | 0 | 29.9781
|  |  | 2019 | 29.9985 | 0 | 0 | 29.9985
|  |  | 2020 | 30.0807 | 0 | 0 | 30.0807
|  |  | 2021 | 29.9985 | 0 | 0 | 29.9985
|  |  | 2022 | 29.9985 | 0 | 0 | 29.9985
|  |  | 2023 | 29.9985 | 0 | 0 | 29.9985
|  |  | 2024 | 30.0807 | 0 | 0 | 30.0807
|  |  | 2025 | 29.9985 | 0 | 0 | 29.9985
|  |  | 2026 | 29.9985 | 0 | 0 | 29.9985
|  |  | 2027 | 29.9905 | 0 | 0 | 29.9905
|  |  | 2028 | 30.0967 | 0 | 0 | 30.0967
|  |  | 2029 | 29.9905 | 0 | 0 | 29.9905
|  |  | 2030 | 29.9905 | 0 | 0 | 29.9905
|  |  | 2031 | 29.9905 | 0 | 0 | 29.9905
|  |  | 2032 | 30.0967 | 0 | 0 | 30.0967
|  |  | 2033 | 29.9905 | 0 | 0 | 29.9905
|  |  | 2034 | 29.9905 | 0 | 0 | 29.9905
|  |  | 2035 | 29.9905 | 0 | 0 | 29.9905
|  |  | 2036 | 30.0967 | 0 | 0 | 30.0967
|  | West Hydro Reserve Capability (aMW) |  |  | 10-minute
|  |  |  | HY_MidCol_P | HY_Rogue | HY_SmallWest | HY_BigFork | HY_Klamath_Dispatch | HY_Klamath_Flat | HY_Klamath_Shape | HY_Lewis_Dispatch | HY_Lewis_Shape | HY_Umpqua_Flat | HY_Umpqua_Shape | [9 empty] | Total |  | Reg Up | Spin
|  |  | 2017 | 26.492 |  |  |  | 18.334 |  |  |  | 250.5281 | [11 empty] | 295.3541 |  |  | 295.3541
|  |  | 2018 | 17.8446 |  |  |  | 18.3082 |  |  |  | 264.6217 | [11 empty] | 300.7745 |  |  | 300.7745
|  |  | 2019 | 7.3595 |  |  |  | 18.4518 |  |  |  | 224.6419 | [11 empty] | 250.4532 |  |  | 250.4532
|  |  | 2020 | 8.0051 |  |  |  | 18.3662 |  |  |  | 266.2954 | [11 empty] | 292.6668 |  |  | 292.6668
|  |  | 2021 | 8.9856 |  |  |  | 0 |  |  |  | 265.2123 | [11 empty] | 274.1979 |  |  | 274.1979
|  |  | 2022 | 9.3555 |  |  |  | 0 |  |  |  | 224.4559 | [11 empty] | 233.8115 |  |  | 233.8115
|  |  | 2023 | 9.4055 |  |  |  | 0 |  |  |  | 265.5334 | [11 empty] | 274.9389 |  |  | 274.9389
|  |  | 2024 | 9.4422 |  |  |  | 0 |  |  |  | 265.4856 | [11 empty] | 274.9279 |  |  | 274.9279
|  |  | 2025 | 9.4083 |  |  |  | 0 |  |  |  | 266.0428 | [11 empty] | 275.4511 |  |  | 275.4511
|  |  | 2026 | 9.3465 |  |  |  | 0 |  |  |  | 264.2055 | [11 empty] | 273.552 |  |  | 273.552
|  |  | 2027 | 9.3894 |  |  |  | 0 |  |  |  | 265.1215 | [11 empty] | 274.5108 |  |  | 274.5108
|  |  | 2028 | 9.4458 |  |  |  | 0 |  |  |  | 266.2146 | [11 empty] | 275.6604 |  |  | 275.6604
|  |  | 2029 | 9.3894 |  |  |  | 0 |  |  |  | 265.1213 | [11 empty] | 274.5107 |  |  | 274.5107
|  |  | 2030 | 9.3637 |  |  |  | 0 |  |  |  | 264.397 | [11 empty] | 273.7607 |  |  | 273.7607
|  |  | 2031 | 9.3894 |  |  |  | 0 |  |  |  | 265.1213 | [11 empty] | 274.5107 |  |  | 274.5107
|  |  | 2032 | 9.4458 |  |  |  | 0 |  |  |  | 266.2146 | [11 empty] | 275.6604 |  |  | 275.6604
|  |  | 2033 | 9.3886 |  |  |  | 0 |  |  |  | 265.1212 | [11 empty] | 274.5098 |  |  | 274.5098
|  |  | 2034 | 9.3637 |  |  |  | 0 |  |  |  | 264.397 | [11 empty] | 273.7607 |  |  | 273.7607
|  |  | 2035 | 9.3894 |  |  |  | 0 |  |  |  | 265.1213 | [11 empty] | 274.5107 |  |  | 274.5107
|  |  | 2036 | 9.4458 |  |  |  | 0 |  |  |  | 266.2146 | [11 empty] | 275.6604 |  |  | 275.6604
|  | East Thermal Reserve Capability (aMW) |  |  | 10-minute | [34 empty] | East Thermal Reserve Capability (aMW) |  |  | 30-minute
|  |  |  | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal/Gas | Coal | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Geo | Geo | Gas | Gas | Gas | Gas |  |  |  | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal | Coal/Gas | Coal | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Geo | Geo | Gas | Gas | Gas | Gas
|  |  |  | Carbon 1 | Carbon 2 | Cholla 4 | Dave Johnston 1 | Dave Johnston 2 | Dave Johnston 3 | Dave Johnston 4 | Hunter 1 | Hunter 2 | Hunter 3 | Huntington 1 | Huntington 2 | Naughton 12 | Naughton 2 | Naughton 3 | Wyodak3 | Currant Creek CC6 | Gadsby 1 | Gadsby 2 | Gadsby 3 | Gadsby 47 | Gadsby 57 | Gadsby 67 | Lake Side 1 CC9 | West Valley 17 | West Valley 27 | West Valley 37 | West Valley 47 | West Valley 57 | Blundell 1 | Blundell 211 | Lake Side 2 CC9 | I_UN_SC_Frm | I_DJ_CC_J1 | I_DJ_SC-FRM | Total |  |  | Carbon 1 | Carbon 2 | Cholla 4 | Dave Johnston 1 | Dave Johnston 2 | Dave Johnston 3 | Dave Johnston 4 | Hunter 1 | Hunter 2 | Hunter 3 | Huntington 1 | Huntington 2 | Naughton 12 | Naughton 2 | Naughton 3 | Wyodak3 | Currant Creek CC6 | Gadsby 1 | Gadsby 2 | Gadsby 3 | Gadsby 47 | Gadsby 57 | Gadsby 67 | Lake Side 1 CC9 | West Valley 17 | West Valley 27 | West Valley 37 | West Valley 47 | West Valley 57 | Blundell 1 | Blundell 211 | Lake Side 2 CC9 | I_UN_SC_Frm | 0 | 0 | Total
|  |  | 2017 | 0 | 0 | 40 | 11.2 | 11.2 | 23.3 | 35 | 37.5 | 24.124 | 40 | 40 | 40 | 10 | 40 | 50 | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243 |  |  |  | 1309.924 |  | 2017 | 0 | 0 | 120 | 11.2 | 11.2 | 23.3 | 35 | 112.5 | 72.372 | 120 | 120 | 120 | 30 | 100 | 100 | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243 |  |  |  | 1945.172
|  |  | 2018 | 0 | 0 | 40 | 11.2 | 11.2 | 23.3 | 35 | 37.5 | 24.124 | 40 | 40 | 40 | 10 | 40 | 50 | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1309.924 |  | 2018 | 0 | 0 | 120 | 11.2 | 11.2 | 23.3 | 35 | 112.5 | 72.372 | 120 | 120 | 120 | 30 | 100 | 100 | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1945.172
|  |  | 2019 |  |  | 40 | 11.2 | 11.2 | 23.3 | 35 | 37.5 | 24.124 | 40 | 40 | 40 | 10 | 40 | 0 | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1259.924 |  | 2019 |  |  | 120 | 11.2 | 11.2 | 23.3 | 35 | 112.5 | 72.372 | 120 | 120 | 120 | 30 | 100 | 0 | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1845.172
|  |  | 2020 |  |  | 40 | 11.2 | 11.2 | 23.3 | 35 | 37.5 | 24.124 | 40 | 40 | 40 | 10 | 40 | 0 | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1259.924 |  | 2020 |  |  | 120 | 11.2 | 11.2 | 23.3 | 35 | 112.5 | 72.372 | 120 | 120 | 120 | 30 | 100 | 0 | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1845.172
|  |  | 2021 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 37.5 | 24.124 | 40 | 40 | 40 | 10 | 40 | 0 | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1219.924 |  | 2021 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 112.5 | 72.372 | 120 | 120 | 120 | 30 | 100 | 0 | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1725.172
|  |  | 2022 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 37.5 | 24.124 | 40 | 40 | 40 | 10 | 40 | 0 | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1219.924 |  | 2022 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 112.5 | 72.372 | 120 | 120 | 120 | 30 | 100 | 0 | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1725.172
|  |  | 2023 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 37.5 | 24.124 | 40 | 40 | 40 | 10 | 40 | 0 | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1219.924 |  | 2023 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 112.5 | 72.372 | 120 | 120 | 120 | 30 | 100 | 0 | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1725.172
|  |  | 2024 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 37.5 | 24.124 | 40 | 40 | 40 | 10 | 40 | 0 | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1219.924 |  | 2024 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 112.5 | 72.372 | 120 | 120 | 120 | 30 | 100 | 0 | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1725.172
|  |  | 2025 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 37.5 | 24.124 | 40 | 40 | 40 | 10 | 40 | 0 | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1219.924 |  | 2025 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 112.5 | 72.372 | 120 | 120 | 120 | 30 | 100 | 0 | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1725.172
|  |  | 2026 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 37.5 | 24.124 | 40 | 40 | 40 | 10 | 40 | 0 | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1219.924 |  | 2026 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 112.5 | 72.372 | 120 | 120 | 120 | 30 | 100 | 0 | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1725.172
|  |  | 2027 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 37.5 | 24.124 | 40 | 40 | 40 | 10 | 40 | 0 | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1219.924 |  | 2027 |  |  | 0 | 11.2 | 11.2 | 23.3 | 35 | 112.5 | 72.372 | 120 | 120 | 120 | 30 | 100 | 0 | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1725.172
|  |  | 2028 |  |  | 0 |  |  |  |  | 37.5 | 24.124 | 40 | 40 | 40 | 10 | 40 | 0 | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1139.224 |  | 2028 |  |  | 0 |  |  |  |  | 112.5 | 72.372 | 120 | 120 | 120 | 30 | 100 | 0 | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 |  |  |  | 1644.472
|  |  | 2029 |  |  | 0 |  |  |  |  | 37.5 | 24.124 | 40 | 40 | 40 | 10 | 40 | 0 | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 | 112 |  |  | 1251.224 |  | 2029 |  |  | 0 |  |  |  |  | 112.5 | 72.372 | 120 | 120 | 120 | 30 | 100 | 0 | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 | 112 |  |  | 1756.472
|  |  | 2030 |  |  | 0 |  |  |  |  | 37.5 | 24.124 | 40 | 40 | 40 |  |  |  | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 | 112 |  |  | 1201.224 |  | 2030 |  |  | 0 |  |  |  |  | 112.5 | 72.372 | 120 | 120 | 120 |  |  |  | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 | 112 |  |  | 1626.472
|  |  | 2031 |  |  | 0 |  |  |  |  | 37.5 | 24.124 | 40 | 40 | 40 |  |  |  | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 | 112 |  |  | 1201.224 |  | 2031 |  |  | 0 |  |  |  |  | 112.5 | 72.372 | 120 | 120 | 120 |  |  |  | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 | 112 |  |  | 1626.472
|  |  | 2032 |  |  | 0 |  |  |  |  | 37.5 | 24.124 | 40 | 40 | 40 |  |  |  | 35.6 | 215 | 25 | 25 | 38 | 30 | 30 | 30 | 236 | [5 empty] | 0 | 0 | 243 | 112 |  |  | 1201.224 |  | 2032 |  |  | 0 |  |  |  |  | 112.5 | 72.372 | 120 | 120 | 120 |  |  |  | 35.6 | 215 | 25 | 25 | 70 | 40 | 40 | 40 | 236 | [5 empty] | 0 | 0 | 243 | 112 |  |  | 1626.472
|  |  | 2033 |  |  | 0 |  |  |  |  | 37.5 | 24.124 | 40 | 40 | 40 |  |  |  | 35.6 | 215 | [6 empty] | 236 | [5 empty] | 0 | 0 | 243 | 112 | 304 | 112 | 1439.224 |  | 2033 |  |  | 0 |  |  |  |  | 112.5 | 72.372 | 120 | 120 | 120 |  |  |  | 35.6 | 215 | [6 empty] | 236 | [5 empty] | 0 | 0 | 243 | 112 | 304 | 112 | 1802.472
|  |  | 2034 |  |  | 0 |  |  |  |  | 37.5 | 24.124 | 40 | 40 | 40 |  |  |  | 35.6 | 215 | [6 empty] | 236 | [5 empty] | 0 | 0 | 243 | 112 | 304 | 112 | 1439.224 |  | 2034 |  |  | 0 |  |  |  |  | 112.5 | 72.372 | 120 | 120 | 120 |  |  |  | 35.6 | 215 | [6 empty] | 236 | [5 empty] | 0 | 0 | 243 | 112 | 304 | 112 | 1802.472
|  |  | 2035 |  |  | 0 |  |  |  |  | 37.5 | 24.124 | 40 | 40 | 40 |  |  |  | 35.6 | 215 | [6 empty] | 236 | [5 empty] | 0 | 0 | 243 | 112 | 304 | 112 | 1439.224 |  | 2035 |  |  | 0 |  |  |  |  | 112.5 | 72.372 | 120 | 120 | 120 |  |  |  | 35.6 | 215 | [6 empty] | 236 | [5 empty] | 0 | 0 | 243 | 112 | 304 | 112 | 1802.472
|  |  | 2036 |  |  | 0 |  |  |  |  | 37.5 | 24.124 | 40 | 40 | 40 |  |  |  | 35.6 | 215 | [6 empty] | 236 | [5 empty] | 0 | 0 | 243 | 112 | 304 | 112 | 1439.224 |  | 2036 |  |  | 0 |  |  |  |  | 112.5 | 72.372 | 120 | 120 | 120 |  |  |  | 35.6 | 215 | [6 empty] | 236 | [5 empty] | 0 | 0 | 243 | 112 | 304 | 112 | 1802.472
|  | West Thermal Reserve Capability (aMW) |  |  | 10-minute | [34 empty] | West Thermal Reserve Capability (aMW) |  |  | 30-minute
|  |  |  | Coal | Coal | Coal | Coal | Gas | Gas | Gas | [31 empty] | Coal | Coal | Coal | Coal | Gas | Gas | Gas
|  |  |  | Jim Bridger 11 | Jim Bridger 21 | Jim Bridger 31 | Jim Bridger 41 | Chehalis CC5 | Hermiston 18 | Hermiston 28 | I_WV_CC_G1 | Total | [29 empty] | Jim Bridger 11 | Jim Bridger 21 | Jim Bridger 31 | Jim Bridger 41 | Chehalis CC5 | Hermiston 18 | Hermiston 28 | I_WV_CC_G1 | Total
|  |  | 2017 | 33 | 33 | 33 | 33 | 218 | 50 | 50 |  | 450 | [28 empty] | 2017 | 99 | 99 | 99 | 99 | 218 | 50 | 50 |  | 714
|  |  | 2018 | 33 | 33 | 33 | 33 | 218 | 50 | 50 |  | 450 | [28 empty] | 2018 | 99 | 99 | 99 | 99 | 218 | 50 | 50 |  | 714
|  |  | 2019 | 33 | 33 | 33 | 33 | 218 | 50 | 50 |  | 450 | [28 empty] | 2019 | 99 | 99 | 99 | 99 | 218 | 50 | 50 |  | 714
|  |  | 2020 | 33 | 33 | 33 | 33 | 218 | 50 | 50 |  | 450 | [28 empty] | 2020 | 99 | 99 | 99 | 99 | 218 | 50 | 50 |  | 714
|  |  | 2021 | 33 | 33 | 33 | 33 | 218 | 50 | 50 |  | 450 | [28 empty] | 2021 | 99 | 99 | 99 | 99 | 218 | 50 | 50 |  | 714
|  |  | 2022 | 33 | 33 | 33 | 33 | 218 | 50 | 50 |  | 450 | [28 empty] | 2022 | 99 | 99 | 99 | 99 | 218 | 50 | 50 |  | 714
|  |  | 2023 | 33 | 33 | 33 | 33 | 218 | 50 | 50 |  | 450 | [28 empty] | 2023 | 99 | 99 | 99 | 99 | 218 | 50 | 50 |  | 714
|  |  | 2024 | 33 | 33 | 33 | 33 | 218 | 50 | 50 |  | 450 | [28 empty] | 2024 | 99 | 99 | 99 | 99 | 218 | 50 | 50 |  | 714
|  |  | 2025 | 33 | 33 | 33 | 33 | 218 | 50 | 50 |  | 450 | [28 empty] | 2025 | 99 | 99 | 99 | 99 | 218 | 50 | 50 |  | 714
|  |  | 2026 | 33 | 33 | 33 | 33 | 218 | 50 | 50 |  | 450 | [28 empty] | 2026 | 99 | 99 | 99 | 99 | 218 | 50 | 50 |  | 714
|  |  | 2027 | 33 | 33 | 33 | 33 | 218 | 50 | 50 |  | 450 | [28 empty] | 2027 | 99 | 99 | 99 | 99 | 218 | 50 | 50 |  | 714
|  |  | 2028 | 33 | 33 | 33 | 33 | 218 | 50 | 50 |  | 450 | [28 empty] | 2028 | 99 | 99 | 99 | 99 | 218 | 50 | 50 |  | 714
|  |  | 2029 |  | 33 | 33 | 33 | 218 | 50 | 50 |  | 417 | [28 empty] | 2029 |  | 99 | 99 | 99 | 218 | 50 | 50 |  | 615
|  |  | 2030 |  | 33 | 33 | 33 | 218 | 50 | 50 | 277 | 694 | [28 empty] | 2030 |  | 99 | 99 | 99 | 218 | 50 | 50 | 277 | 892
|  |  | 2031 |  | 33 | 33 | 33 | 218 | 50 | 50 | 277 | 694 | [28 empty] | 2031 |  | 99 | 99 | 99 | 218 | 50 | 50 | 277 | 892
|  |  | 2032 |  | 33 | 33 | 33 | 218 | 50 | 50 | 277 | 694 | [28 empty] | 2032 |  | 99 | 99 | 99 | 218 | 50 | 50 | 277 | 892
|  |  | 2033 |  |  | 33 | 33 | 218 | 50 | 50 | 277 | 661 | [28 empty] | 2033 |  |  | 99 | 99 | 218 | 50 | 50 | 277 | 793
|  |  | 2034 |  |  | 33 | 33 | 218 | 50 | 50 | 277 | 661 | [28 empty] | 2034 |  |  | 99 | 99 | 218 | 50 | 50 | 277 | 793
|  |  | 2035 |  |  | 33 | 33 | 218 | 50 | 50 | 277 | 661 | [28 empty] | 2035 |  |  | 99 | 99 | 218 | 50 | 50 | 277 | 793
|  |  | 2036 |  |  | 33 | 33 | 218 | 50 | 50 | 277 | 661 | [28 empty] | 2036 |  |  | 99 | 99 | 218 | 50 | 50 | 277 | 793
|  |  |  | East |  |  |  | West
|  |  | Year | Coal | Gas | Hydro | Total | Coal | Gas | Hydro | Total |  |  | East |  |  |  | West
|  |  | 2017 | 437.924 | 872 | 30.0009 | 1339.9249 | 132 | 318 | 295.3541 | 745.3541 |  |  | Coal | Gas | Hydro |  | Coal | Gas | Hydro
|  |  | 2018 | 437.924 | 872 | 29.9781 | 1339.9021 | 132 | 318 | 300.7745 | 750.7745 |  | 2017 | 32.68% | 65.08% | 2.239% |  | 17.71% | 42.66% | 39.63%
|  |  | 2019 | 387.924 | 872 | 29.9985 | 1289.9225 | 132 | 318 | 250.4532 | 700.4532 |  | 2018 | 32.68% | 65.08% | 2.237% |  | 17.58% | 42.36% | 40.06%
|  |  | 2020 | 387.924 | 872 | 30.0807 | 1290.0047 | 132 | 318 | 292.6668 | 742.6668 |  | 2019 | 30.07% | 67.6% | 2.326% |  | 18.84% | 45.4% | 35.76%
|  |  | 2021 | 347.924 | 872 | 29.9985 | 1249.9225 | 132 | 318 | 274.1979 | 724.1979 |  | 2020 | 30.07% | 67.6% | 2.332% |  | 17.77% | 42.82% | 39.41%
|  |  | 2022 | 347.924 | 872 | 29.9985 | 1249.9225 | 132 | 318 | 233.8115 | 683.8115 |  | 2021 | 27.84% | 69.76% | 2.4% |  | 18.23% | 43.91% | 37.86%
|  |  | 2023 | 347.924 | 872 | 29.9985 | 1249.9225 | 132 | 318 | 274.9389 | 724.9389 |  | 2022 | 27.84% | 69.76% | 2.4% |  | 19.3% | 46.5% | 34.19%
|  |  | 2024 | 347.924 | 872 | 30.0807 | 1250.0047 | 132 | 318 | 274.9279 | 724.9279 |  | 2023 | 27.84% | 69.76% | 2.4% |  | 18.21% | 43.87% | 37.93%
|  |  | 2025 | 347.924 | 872 | 29.9985 | 1249.9225 | 132 | 318 | 275.4511 | 725.4511 |  | 2024 | 27.83% | 69.76% | 2.406% |  | 18.21% | 43.87% | 37.92%
|  |  | 2026 | 347.924 | 872 | 29.9985 | 1249.9225 | 132 | 318 | 273.552 | 723.552 |  | 2025 | 27.84% | 69.76% | 2.4% |  | 18.2% | 43.83% | 37.97%
|  |  | 2027 | 347.924 | 872 | 29.9905 | 1249.9145 | 132 | 318 | 274.5108 | 724.5108 |  | 2026 | 27.84% | 69.76% | 2.4% |  | 18.24% | 43.95% | 37.81%
|  |  | 2028 | 267.224 | 872 | 30.0967 | 1169.3207 | 132 | 318 | 275.6604 | 725.6604 |  | 2027 | 27.84% | 69.76% | 2.399% |  | 18.22% | 43.89% | 37.89%
|  |  | 2029 | 267.224 | 984 | 29.9905 | 1281.2145 | 99 | 318 | 274.5107 | 691.5107 |  | 2028 | 22.85% | 74.57% | 2.574% |  | 18.19% | 43.82% | 37.99%
|  |  | 2030 | 217.224 | 984 | 29.9905 | 1231.2145 | 99 | 318 | 273.7607 | 690.7607 |  | 2029 | 20.86% | 76.8% | 2.341% |  | 14.32% | 45.99% | 39.7%
|  |  | 2031 | 217.224 | 984 | 29.9905 | 1231.2145 | 99 | 318 | 274.5107 | 691.5107 |  | 2030 | 17.64% | 79.92% | 2.436% |  | 14.33% | 46.04% | 39.63%
|  |  | 2032 | 217.224 | 984 | 30.0967 | 1231.3207 | 99 | 318 | 275.6604 | 692.6604 |  | 2031 | 17.64% | 79.92% | 2.436% |  | 14.32% | 45.99% | 39.7%
|  |  | 2033 | 217.224 | 1222 | 29.9905 | 1469.2145 | 66 | 318 | 274.5098 | 658.5098 |  | 2032 | 17.64% | 79.91% | 2.444% |  | 14.29% | 45.91% | 39.8%
|  |  | 2034 | 217.224 | 1222 | 29.9905 | 1469.2145 | 66 | 318 | 273.7607 | 657.7607 |  | 2033 | 14.79% | 83.17% | 2.041% |  | 10.02% | 48.29% | 41.69%
|  |  | 2035 | 217.224 | 1222 | 29.9905 | 1469.2145 | 66 | 318 | 274.5107 | 658.5107 |  | 2034 | 14.79% | 83.17% | 2.041% |  | 10.03% | 48.35% | 41.62%
|  |  | 2036 | 217.224 | 1222 | 30.0967 | 1469.3207 | 66 | 318 | 275.6604 | 659.6604 |  | 2035 | 14.79% | 83.17% | 2.041% |  | 10.02% | 48.29% | 41.69%
|  |  |  | Supply: Coal | Supply: Gas | Supply: Hydro |  | Supply: Coal | Supply: Gas | Supply: Hydro
Note on AN77: p07242: New Built resources
Note on AP77: p07242: New Built resources
Note on AQ77: p07242: New Built resources
Note on CB77: p07242: New Built resources
Note on CD77: p07242: New Built resources
Note on CE77: p07242: New Built resources
Note on W80: p07242: Gas Conversion Unit from 2015 forward.
Note on BK80: p07242: Gas Conversion Unit from 2015 forward.