## Table I.1 I.2
Table I.1 - Expansion Resource Additions by PRM for Summer
Summer
PRM (%) | DSM Capacity at System Peak | DSM Class 1 | FOT | FOT Flat | SCCT | CCCT | Total | FOT
10 | 380.22 | 0 | 550.496 | 175.905 | 0 | 0 | 1106.621 | 726.401
11 | 373.95 | 0 | 650.724 | 176.175 | 0 | 0 | 1200.849 | 826.899
12 | 380.09 | 0 | 738.431 | 175.947 | 0 | 0 | 1294.468 | 914.378
13 | 384.29 | 0 | 828.258 | 175.569 | 0 | 0 | 1388.117 | 1003.827
14 | 394.04 | 0 | 912.197 | 175.027 | 0 | 0 | 1481.264 | 1087.224
15 | 399.56 | 0 | 1000.388 | 174.648 | 0 | 0 | 1574.596 | 1175.036
16 | 382.13 | 0 | 1112.304 | 175.585 | 0 | 0 | 1670.019 | 1287.889
17 | 425.43 | 25.43 | 1134.088 | 173.89 | 0 | 0 | 1758.838 | 1307.978
18 | 431.1 | 112.5 | 1135.917 | 172.136 | 0 | 0 | 1851.653 | 1308.053
19 | 396.08 | 0 | 982.224 | 174.648 | 0 | 454.41 | 2007.362 | 1156.872
20 | 379.65 | 0 | 1093.313 | 175.963 | 0 | 454.41 | 2103.336 | 1269.276
Table I.2 - Expansion Resource Additions by PRM for Winter
Winter
PRM (%) | DSM Capacity at System Peak | DSM Class 1 | FOT | FOT Flat | SCCT | CCCT | Total
10 | 239.76 | 0 | 26.292 | 175.905 | 0 | 0 | 441.957 | 202.197
11 | 236.94 | 0 | 33.52 | 176.175 | 0 | 0 | 446.635 | 209.695
12 | 239.66 | 0 | 40.695 | 175.947 | 0 | 0 | 456.302 | 216.642
13 | 243.37 | 0 | 47.8 | 175.569 | 0 | 0 | 466.739 | 223.369
14 | 250.48 | 0 | 54.828 | 175.027 | 0 | 0 | 480.335 | 229.855
15 | 253.06 | 0 | 69.648 | 174.648 | 0 | 0 | 497.356 | 244.296
16 | 240.68 | 0 | 86.016 | 175.585 | 0 | 0 | 502.281 | 261.601
17 | 258.93 | 25.43 | 100.557 | 173.89 | 0 | 0 | 558.807 | 274.447
18 | 265.76 | 112.5 | 92.784 | 172.136 | 0 | 0 | 643.18 | 264.92
19 | 248.17 | 0 | 132.522 | 174.648 | 0 | 454.41 | 1009.75 | 307.17
20 | 238.63 | 0 | 149.065 | 175.963 | 0 | 454.41 | 1018.068 | 325.028

## Tables I.3-4, and Figs I.2-4
| Table I.3 - Expected Reliability Metrics by PRM | [6 empty] | Table I.4 - Fitted Reliability Metrics by PRM
|  | Before NWPP Adjustment |  |  | After NWPP Adjustment |  |  |  | Before NWPP Adjustment |  |  | After NWPP Adjustment
Study | PRM (%) | Simulated Energy Not Served (GWh) | LOLH (<2.4 target year) (Hour) | Loss of Load Episodes | EUE (GWh) | LOLH (Hour) | Modeled Loss of Load Episodes | PRM (%) | EUE (GWh) | LOLH (<2.4 target year) (Hour) | Modeled Loss of Load Episodes | EUE (GWh) | LOLH (Hour) | Modeled Loss of Load Episodes
| 10 | 78.8534 | 0.93771 | 0.69029 | 20.8065 | 0.24743 | 0.15029 | 10 | 91.231 | 0.9739 | 0.7102 | 24.411 | 0.2636 | 0.1645
| 11 | 80.1659 | 0.92914 | 0.68171 | 21.348 | 0.24743 | 0.15029 | 11 | 81.3744 | 0.93855 | 0.6901 | 21.5414 | 0.24904 | 0.1541
| 12 | 78.8896 | 0.938 | 0.69057 | 20.8097 | 0.24743 | 0.15029 | 12 | 75.6087 | 0.91787 | 0.67834 | 19.8627 | 0.24053 | 0.14802
| 13 | 77.957 | 0.92057 | 0.68171 | 20.2272 | 0.23886 | 0.15029 | 13 | 71.5179 | 0.9032 | 0.67 | 18.6717 | 0.23449 | 0.14371
| 14 | 75.7859 | 0.902 | 0.66314 | 20.0687 | 0.23886 | 0.15029 | 14 | 68.3448 | 0.89182 | 0.66353 | 17.7479 | 0.2298 | 0.14036
| 15 | 74.7383 | 0.90286 | 0.664 | 19.7725 | 0.23886 | 0.15029 | 15 | 65.7522 | 0.88252 | 0.65824 | 16.9931 | 0.22597 | 0.13762
| 16 | 78.4431 | 0.938 | 0.69057 | 20.692 | 0.24743 | 0.15029 | 16 | 63.5602 | 0.87466 | 0.65377 | 16.3549 | 0.22274 | 0.13531
| 17 | 71.7578 | 0.92057 | 0.68171 | 18.6187 | 0.23886 | 0.15029 | 17 | 61.6613 | 0.86785 | 0.6499 | 15.8021 | 0.21993 | 0.13331
| 18 | 70.5355 | 0.912 | 0.68171 | 17.8107 | 0.23029 | 0.14171 | 18 | 59.9865 | 0.86184 | 0.64648 | 15.3145 | 0.21746 | 0.13154
| 19 | 33.25 | 0.77771 | 0.60086 | 7.5613 | 0.17686 | 0.097143 | 19 | 58.4882 | 0.85647 | 0.64343 | 14.8783 | 0.21525 | 0.12996
| 20 | 34.2889 | 0.76086 | 0.57543 | 8.3566 | 0.18543 | 0.097143 | 20 | 57.1329 | 0.85161 | 0.64066 | 14.4837 | 0.21324 | 0.12853
Figure I.2 - Expected and Fitted Relationship of EUE to PRM
Figure I.3 - Expected and Fitted Relationship of LOLH to PRM
Figure I.4 - Simulated Relationship of Loss of Load Episodes to PRM

## NWPP Adj
Study | PRM (%) | Simulated Energy Not Served (GWh) | Simulated Expected Loss of Load Hours | Simulated Loss of Load Episodes | Energy Served through Reserve Sharing (GWh) | EUE (GWh) | LOLH |  | Reserve sharing divided by simulated EUE
|  | G | H | O | G / H * O | N = G - R | H - O
| 10 | 78.8534 | 0.93771 | 0.69029 | 58.0469 | 20.8065 | 0.24743 |  | 73.61%
| 11 | 80.1659 | 0.92914 | 0.68171 | 58.8179 | 21.348 | 0.24743 |  | 73.37%
| 12 | 78.8896 | 0.938 | 0.69057 | 58.0798 | 20.8097 | 0.24743 |  | 73.62%
| 13 | 77.957 | 0.92057 | 0.68171 | 57.7298 | 20.2272 | 0.23886 |  | 74.05%
| 14 | 75.7859 | 0.902 | 0.66314 | 55.7171 | 20.0687 | 0.23886 |  | 73.52%
| 15 | 74.7383 | 0.90286 | 0.664 | 54.9658 | 19.7725 | 0.23886 |  | 73.54%
| 16 | 78.4431 | 0.938 | 0.69057 | 57.7511 | 20.692 | 0.24743 |  | 73.62%
| 17 | 71.7578 | 0.92057 | 0.68171 | 53.1391 | 18.6187 | 0.23886 |  | 74.05%
| 18 | 70.5355 | 0.912 | 0.68171 | 52.7248 | 17.8107 | 0.23029 |  | 74.75%
| 19 | 33.25 | 0.77771 | 0.60086 | 25.6887 | 7.5613 | 0.17686 |  | 77.26%
| 20 | 34.2889 | 0.76086 | 0.57543 | 25.9324 | 8.3566 | 0.18543 |  | 75.63%
[8 empty] | avg | 74.28%