## Table 6.1
Table - 2017 Supply Side Table (2016$)
| Description |  | Resource Characteristics |  |  |  | Costs |  |  | Operating Characteristics |  |  |  | Environmental
| Fuel | Resource | Elevation (AFSL) | Net Capacity (MW) | Commercial Operation Year | Design Life (yrs) | Base Capital ($/KW) | Var O&M ($/MWh) | Fixed O&M ($/KW-yr) | Average Full Load Heat Rate (HHV Btu/KWh)/Efficiency | EFOR (%) | POR (%) | Water Consumed (Gal/MWh) | SO2 (lbs/MMBtu) | NOx (lbs/MMBtu) | Hg (lbs/TBTu) | CO2 (lbs/MMBtu)
1 | Natural Gas | SCCT Aero x3, ISO | 0 | 141.9097 | 2021.0845 | 30 | 1420.5567 | 7.54 | 27.14 | 9204 | 2.6 | 3.85 | 58 | 0.0006 | 0.009 | 0.255 | 117
2 | Natural Gas | Intercooled SCCT Aero x2, ISO | 0 | 220.6745 | 2021.0845 | 30 | 1036.2994 | 5.05 | 18.78 | 8981 | 2.9 | 3.85 | 80 | 0.0006 | 0.009 | 0.255 | 117
3 | Natural Gas | SCCT Frame "F" x1, ISO | 0 | 240.2941 | 2021.0845 | 35 | 583.7288 | 5.5 | 13.28 | 9604 | 2.7 | 3.85 | 20 | 0.0006 | 0.009 | 0.255 | 117
4 | Natural Gas | IC Recips x 6, ISO | 0 | 110.5535 | 2021.0845 | 35 | 1572.4256 | 7.45 | 29.82 | 8279 | 2.5 | 5 | 5 | 0.0006 | 0.0288 | 0.255 | 117
5 | Natural Gas | CCCT Dry "G/H", 1x1, ISO | 0 | 407.1465 | 2021.5036 | 40 | 1404.8872 | 1.76 | 20.52 | 6363 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
6 | Natural Gas | CCCT Dry "G/H", DF, 1x1, ISO | 0 | 51.0003 | 2021.5036 | 40 | 443.0343 | 0.15 | 5.39 | 8865 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
7 | Natural Gas | CCCT Dry "G/H", 2x1, ISO | 0 | 815.6922 | 2022.5035 | 40 | 1042.9757 | 1.67 | 13.79 | 6352 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
8 | Natural Gas | CCCT Dry "G/H", DF, 2x1, ISO | 0 | 101.9939 | 2022.5035 | 40 | 348.0646 | 0.16 | 4.44 | 8812 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
9 | Natural Gas | CCCT Dry "J/HA.02", 1x1, ISO | 0 | 498.03 | 2021.5036 | 40 | 1226.2066 | 1.7 | 17.66 | 6317 | 2.5 | 3.8 | 0 | 0.0006 | 0.0072 | 0.255 | 117
10 | Natural Gas | CCCT Dry "J/HA.02", DF, 1x1, ISO | 0 | 62.9999 | 2021.5036 | 40 | 378.1246 | 0.16 | 4.86 | 8878 | 0.8 | 3.8 | 0 | 0.0006 | 0.0072 | 0.255 | 117
11 | Natural Gas | CCCT Dry, "J/HA.02" 2X1, ISO | 0 | 997.6192 | 2022.5035 | 40 | 913.0611 | 1.62 | 12 | 6308 | 2.5 | 3.8 | 0 | 0.0006 | 0.0072 | 0.255 | 117
12 | Natural Gas | CCCT Dry "J/HA.02", DF, 2X1, ISO | 0 | 125.9959 | 2022.5035 | 40 | 301.6021 | 0.16 | 4.05 | 8830 | 0.8 | 3.8 | 0 | 0.0006 | 0.0072 | 0.255 | 117
13 | Natural Gas | SCCT Aero x3 | 1500 | 137.7394 | 2021.0845 | 30 | 1463.5665 | 7.76 | 27.96 | 9169 | 2.6 | 3.85 | 58 | 0.0006 | 0.009 | 0.255 | 117
14 | Natural Gas | Intercooled SCCT Aero x2 | 1500 | 208.4491 | 2021.0845 | 30 | 1097.0774 | 5.35 | 19.88 | 9000 | 2.9 | 3.85 | 80 | 0.0006 | 0.009 | 0.255 | 117
15 | Natural Gas | SCCT Frame "F" x1 | 1500 | 227.6546 | 2021.0845 | 35 | 616.1377 | 5.81 | 14.02 | 9604 | 2.7 | 3.85 | 20 | 0.0006 | 0.009 | 0.255 | 117
16 | Natural Gas | IC Recips x 6 | 1500 | 110.5535 | 2021.0845 | 35 | 1572.4256 | 7.45 | 29.82 | 8279 | 2.5 | 5 | 5 | 0.0006 | 0.0288 | 0.255 | 117
17 | Natural Gas | CCCT Dry "G/H", 1x1 | 1500 | 385.3535 | 2021.5036 | 40 | 1484.3381 | 1.86 | 21.68 | 6362 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
18 | Natural Gas | CCCT Dry "G/H", DF, 1x1 | 1500 | 51.0037 | 2021.5036 | 40 | 443.0044 | 0.15 | 5.39 | 9012 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
19 | Natural Gas | CCCT Dry "G/H", 2x1 | 1500 | 771.8273 | 2022.5035 | 40 | 1102.2506 | 1.77 | 14.57 | 6353 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
20 | Natural Gas | CCCT Dry "G/H", DF, 2x1 | 1500 | 101.9937 | 2022.5035 | 40 | 348.0655 | 0.16 | 4.44 | 8969 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
21 | Natural Gas | CCCT Dry "J/HA.02", 1x1 | 1500 | 470.9438 | 2021.5036 | 40 | 1296.7314 | 1.8 | 18.67 | 6317 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
22 | Natural Gas | CCCT Dry "J/HA.02", DF, 1x1 | 1500 | 63.004 | 2021.5036 | 40 | 378.1 | 0.16 | 4.86 | 9035 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
23 | Natural Gas | CCCT Dry, "J/HA.02" 2X1 | 1500 | 943.7244 | 2022.5035 | 40 | 965.2047 | 1.71 | 12.69 | 6304 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
24 | Natural Gas | CCCT Dry "J/HA.02", DF, 2X1 | 1500 | 126.0048 | 2022.5035 | 40 | 301.5809 | 0.16 | 4.05 | 8906 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
25 | Natural Gas | SCCT Aero x3 | 3000 | 130.2074 | 2021.0845 | 30 | 1548.2276 | 8.21 | 29.58 | 9183 | 2.6 | 3.85 | 58 | 0.0006 | 0.009 | 0.255 | 117
26 | Natural Gas | Intercooled SCCT Aero x2 | 3000 | 196.4388 | 2021.0845 | 30 | 1164.1529 | 5.67 | 21.1 | 9016 | 2.9 | 3.85 | 80 | 0.0006 | 0.009 | 0.255 | 117
27 | Natural Gas | SCCT Frame "F" x1 | 3000 | 215.6017 | 2021.0845 | 35 | 650.5821 | 6.13 | 14.81 | 9611 | 2.7 | 3.85 | 20 | 0.0006 | 0.009 | 0.255 | 117
28 | Natural Gas | IC Recips x 6 | 3000 | 110.5535 | 2021.0845 | 35 | 1572.4256 | 7.45 | 29.82 | 8279 | 2.5 | 5 | 5 | 0.0006 | 0.0288 | 0.255 | 117
29 | Natural Gas | CCCT Dry "G/H", 1x1 | 3000 | 364.5319 | 2021.5036 | 40 | 1569.1214 | 1.97 | 22.92 | 6366 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
30 | Natural Gas | CCCT Dry "G/H", DF, 1x1 | 3000 | 51.0013 | 2021.5036 | 40 | 443.0253 | 0.15 | 5.39 | 9055 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
31 | Natural Gas | CCCT Dry "G/H", 2x1 | 3000 | 730.7083 | 2022.5035 | 40 | 1164.2775 | 1.86 | 15.39 | 6352 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
32 | Natural Gas | CCCT Dry "G/H", DF, 2x1 | 3000 | 101.9466 | 2022.5035 | 40 | 348.2264 | 0.16 | 4.44 | 9012 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
33 | Natural Gas | CCCT Dry "J/HA.02", 1x1 | 3000 | 445.5988 | 2021.5036 | 40 | 1370.4877 | 1.9 | 19.73 | 6321 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
34 | Natural Gas | CCCT Dry "J/HA.02", DF, 1x1 | 3000 | 62.9978 | 2021.5036 | 40 | 378.1374 | 0.16 | 4.86 | 9087 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
35 | Natural Gas | CCCT Dry, "J/HA.02" 2X1 | 3000 | 892.9227 | 2022.5035 | 40 | 1020.1188 | 1.81 | 13.41 | 6308 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
36 | Natural Gas | CCCT Dry "J/HA.02", DF, 2X1 | 3000 | 126.0006 | 2022.5035 | 40 | 301.591 | 0.16 | 4.05 | 9039 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
37 | Natural Gas | SCCT Aero x3 | 5050 | 120.8637 | 2021.0845 | 30 | 1667.9175 | 8.85 | 31.86 | 9189 | 2.6 | 3.85 | 58 | 0.0006 | 0.009 | 0.255 | 117
38 | Natural Gas | Intercooled SCCT Aero x2 | 5050 | 181.6303 | 2021.0845 | 30 | 1259.0673 | 6.14 | 22.82 | 9032 | 2.9 | 3.85 | 80 | 0.0006 | 0.009 | 0.255 | 117
39 | Natural Gas | SCCT Frame "F" x1 | 5050 | 199.9241 | 2021.0845 | 35 | 701.5991 | 6.61 | 15.97 | 9614 | 2.7 | 3.85 | 20 | 0.0006 | 0.009 | 0.255 | 117
40 | Natural Gas | IC Recips x 6 | 5050 | 110.5535 | 2021.0845 | 35 | 1572.4256 | 7.45 | 29.82 | 8286 | 2.5 | 5 | 5 | 0.0006 | 0.0288 | 0.255 | 117
41 | Natural Gas | CCCT Dry "G/H", 1x1 | 5050 | 337.7907 | 2021.5036 | 40 | 1693.3409 | 2.12 | 24.74 | 6374 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
42 | Natural Gas | CCCT Dry "G/H", DF, 1x1 | 5050 | 51.0193 | 2021.5036 | 40 | 442.8693 | 0.15 | 5.39 | 9172 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
43 | Natural Gas | CCCT Dry "G/H", 2x1 | 5050 | 676.5813 | 2022.5035 | 40 | 1257.4204 | 2.01 | 16.63 | 6365 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
44 | Natural Gas | CCCT Dry "G/H", DF, 2x1 | 5050 | 102.0032 | 2022.5035 | 40 | 348.0331 | 0.16 | 4.44 | 9141 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
45 | Natural Gas | CCCT Dry "J/HA.02", 1x1 | 5050 | 413.5678 | 2021.5036 | 40 | 1476.6324 | 2.05 | 21.26 | 6326 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
46 | Natural Gas | CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 63.0086 | 2021.5036 | 40 | 378.0723 | 0.16 | 4.86 | 9211 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
47 | Natural Gas | CCCT Dry, "J/HA.02" 2X1 | 5050 | 828.3187 | 2022.5035 | 40 | 1099.6822 | 1.95 | 14.45 | 6317 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
48 | Natural Gas | CCCT Dry "J/HA.02", DF, 2X1 | 5050 | 126.005 | 2022.5035 | 40 | 301.5804 | 0.16 | 4.05 | 9158 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
49 | Natural Gas | SCCT Aero x3 | 6500 | 111.4125 | 2021.0845 | 30 | 1809.4081 | 9.6 | 34.56 | 9195 | 2.6 | 3.85 | 58 | 0.0006 | 0.009 | 0.255 | 117
50 | Natural Gas | Intercooled SCCT Aero x2 | 6500 | 172.6999 | 2021.0845 | 30 | 1324.1743 | 6.45 | 24 | 9003 | 2.9 | 3.85 | 80 | 0.0006 | 0.009 | 0.255 | 117
51 | Natural Gas | SCCT Frame "F" x1 | 6500 | 189.8403 | 2021.0845 | 35 | 738.8661 | 6.96 | 16.81 | 9605 | 2.7 | 3.85 | 20 | 0.0006 | 0.009 | 0.255 | 117
52 | Natural Gas | IC Recips x 6 | 6500 | 106.1894 | 2021.0845 | 35 | 1637.0477 | 7.75 | 31.04 | 8377 | 2.5 | 5 | 5 | 0.0006 | 0.0288 | 0.255 | 117
53 | Natural Gas | CCCT Dry "G/H", 1x1 | 6500 | 318.9379 | 2021.5036 | 40 | 1793.4362 | 2.25 | 26.2 | 6395 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
54 | Natural Gas | CCCT Dry "G/H", DF, 1x1 | 6500 | 51.0052 | 2021.5036 | 40 | 442.9914 | 0.15 | 5.39 | 9524 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
55 | Natural Gas | CCCT Dry "G/H", 2x1 | 6500 | 638.8732 | 2022.5035 | 40 | 1331.6368 | 2.13 | 17.61 | 6385 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
56 | Natural Gas | CCCT Dry "G/H", DF, 2x1 | 6500 | 102.0197 | 2022.5035 | 40 | 347.9768 | 0.16 | 4.44 | 9461 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
57 | Natural Gas | CCCT Dry "J/HA.02", 1x1 | 6500 | 393.7563 | 2021.5036 | 40 | 1550.928 | 2.15 | 22.33 | 6336 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
58 | Natural Gas | CCCT Dry "J/HA.02", DF, 1x1 | 6500 | 63.0098 | 2021.5036 | 40 | 378.0653 | 0.16 | 4.86 | 9524 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
59 | Natural Gas | CCCT Dry, "J/HA.02" 2X1 | 6500 | 788.6039 | 2022.5035 | 40 | 1155.0631 | 2.05 | 15.18 | 6327 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
60 | Natural Gas | CCCT Dry "J/HA.02", DF, 2X1 | 6500 | 125.936 | 2022.5035 | 40 | 301.7457 | 0.16 | 4.06 | 9469 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117
| Description |  | Resource Characteristics |  |  |  | Costs |  |  | Operating Characteristics |  |  |  | Environmental
| Fuel | Resource | Elevation (AFSL) | Net Capacity (MW) | Commercial Operation Year | Design Life (yrs) | Base Capital ($/KW) | Var O&M ($/MWh) | Fixed O&M ($/KW-yr) | Average Full Load Heat Rate (HHV Btu/KWh)/Efficiency | EFOR (%) | POR (%) | Water Consumed (Gal/MWh) | SO2 (lbs/MMBtu) | NOx (lbs/MMBtu) | Hg (lbs/TBTu) | CO2 (lbs/MMBtu)
61 | Coal | SCPC with CCS | 4500 | 526 | 2034 | 40 | 6077.664 | 6.71 | 69.2162 | 13087 | 5 | 5 | 1004.2373 | 0.0085 | 0.07 | 0.022222 | 20.5352
62 | Coal | IGCC with CCS | 4500 | 466 | 2034 | 40 | 5884.4667 | 11.28 | 55.7752 | 10823 | 8 | 7 | 394.0678 | 0.0085 | 0.05 | 0.33333 | 20.5352
63 | Coal | PC CCS retrofit @ 500 MW | 4500 | -139 | 2031 | 20 | 1334.3443 | 6.2017 | 74.5171 | 14372 | 5 | 5 | 1004.2373 | 0.005 | 0.07 | 1.2 | 20.5352
64 | Coal | SCPC with CCS | 6500 | 692 | 2034 | 40 | 6882.6526 | 7.26 | 64.2924 | 13242 | 5 | 5 | 1004.2373 | 0.0085 | 0.07 | 0.022222 | 20.5352
65 | Coal | IGCC with CCS | 6500 | 456 | 2034 | 40 | 6663.0057 | 13.52 | 60.7619 | 11047 | 8 | 7 | 394.0678 | 0.0085 | 0.05 | 0.33333 | 20.5352
66 | Coal | PC CCS retrofit @ 500 MW | 6500 | -139 | 2031 | 20 | 1511.0786 | 6.71 | 69.2162 | 14372 | 5 | 5 | 1004.2373 | 0.005 | 0.07 | 1.2 | 20.5352
67 | Geothermal | Blundell Dual Flash 90% CF | 4500 | 35 | 2021.0845 | 40 | 6130.8225 | 1.12 | 100.51 | n/a | 5 | 5 | 10 | n/a | n/a | n/a | n/a
68 | Geothermal | Greenfield Binary 90% CF | 4500 | 43 | 2022.5035 | 40 | 6793.2297 | 1.1246 | 100.5063 | n/a | 5 | 5 | 270 | n/a | n/a | n/a | n/a
69 | Geothermal | Generic Geothermal PPA 90% CF | 4500 | 30 | 2021.0845 | 20 | 0 | 77.34 | 0 | n/a | 5 | 5 | 270 | n/a | n/a | n/a | n/a
70 | Wind | 2.0 MW turbine 38% CF WA | 1500 | 100 | 2022.0022 | 30 | 1799.7506 | 0 | 36.45 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a
71 | Wind | 2.0 MW turbine 38% CF OR | 1500 | 100 | 2022.0022 | 30 | 1773.9008 | 0 | 36.45 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a
72 | Wind | 2.0 MW turbine 38% CF ID | 4500 | 100 | 2022.0022 | 30 | 1811.0329 | 0 | 36.45 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a
73 | Wind | 2.0 MW turbine 31% CF UT | 4500 | 100 | 2022.0022 | 30 | 1735.3716 | 0 | 36.45 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a
74 | Wind | 3.3 MW turbine 43% CF WY | 6500 | 100 | 2022.0022 | 30 | 1737.2477 | 0.65 | 36.45 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a
84 | Solar | PV Poly-Si Fixed Tilt 26.8% AC CF (1.35 MWdc/Mwac) UT | 4500 | 50 | 2018.9998 | 25 | 1723.7488 | 0 | 18.45 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a
85 | Solar | PV Poly-Si Single Tracking 31.1% AC CF (1.25 MWdc/Mwac) UT | 4500 | 50 | 2018.9998 | 25 | 1822.4072 | 0 | 19.41 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a
86 | Solar | PV Poly-Si Fixed Tilt 24.9% AC CF (1.35 MWdc/Mwac) OR | 4800 | 50 | 2019 | 25 | 1761.8948 | 0 | 18.47 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a
87 | Solar | PV Poly-Si Single Tracking 28.8% AC CF (1.25 MWdc/Mwac) OR | 4800 | 50 | 2019 | 25 | 1856.7386 | 0 | 19.44 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a
88 | Solar | CSP Trough w Natural Gas | 4500 | 100 | 2022 | 30 | 6447.5397 | 0 | 68.4642 | 11750 | Included with CF | 0 | 725 | n/a | n/a | n/a | n/a
89 | Solar | CSP Tower 24% CF | 4500 | 100 | 2022 | 30 | 6141.4654 | 0 | 68.4642 | n/a | Included with CF | 0 | 725 | n/a | n/a | n/a | n/a
90 | Solar | CSP Tower Molten Salt 30% CF | 4500 | 100 | 2022 | 30 | 7367.0328 | 0 | 68.4642 | n/a | Included with CF | 0 | 750 | n/a | n/a | n/a | n/a
91 | Biomass | Forestry Byproduct | 1500 | 5 | 2022.0022 | 30 | 4383.3025 | 0.99 | 42.04 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.4 | 205
92 | Storage | Pumped Storage 1 (3,800 MWh) | 4457 | 393.3 | 2022.0022 | 50 | 3468.3873 | 0 | 21.1 | 77% | 3 | 5.8 | 0 | 0 | 0 | 0 | 0
93 | Storage | Pumped Storage 2 (12,000 MWh) | 580 | 1200 | 2022.0022 | 50 | 3600.6916 | 0 | 15.58 | 77% | 3 | 5.8 | 0 | 0 | 0 | 0 | 0
94 | Storage | Pumped Storage 3 (7,000 MWh) | 6359 | 700 | 2017 | 50 | 2860.7143 | 0 | 16.86 | 77% | 3 | 5.8 | 0 | 0 | 0 | 0 | 0
95 | Storage | CAES (15,360 MWh) | 4640 | 320 | 2021.0024 | 30 | 2138.2486 | 0.77 | 18.9 | 4227 | 3 | 1.5 | 0 | 0.001 | 0.009 | 0 | 117
96 | Nuclear | Advanced Fission | 5000 | 2234 | 2024.7502 | 40 | 6524.1573 | 11.37 | 98.35 | 10710 | 7.7 | 7.3 | 96.0028 | 0 | 0 | 0 | 0
97 | Nuclear | Small Modular Reactor x 12 | 5000 | 570 | 2030.7524 | 40 | 9675.8543 | 15 | 167.77 | 10710 | 7.7 | 7.3 | 64.5435 | 0 | 0 | 0 | 0

## Table 6.2 P1
|  | Capital Cost $/kW |  |  | Fixed Cost
Supply Side Resource Options Mid-Calendar Year 2016 Dollars ($) | Elevation (AFSL) |  |  |  | Fixed O&M $/kW-Yr
Resource Description |  | Total Capital Cost | Payment Factor | Annual Payment ($/kW-Yr) | O&M | Capitalized Premium | O&M Capitalized | Gas Transportation | Total | Total Fixed ($/kW-Yr)
SCCT Aero x3, ISO | 0 | 1420.5567 | 7.871% | 111.8134 | 27.14 | 1.331% | 0.36115 | 32.9684 | 60.4695 | 172.2829
Intercooled SCCT Aero x2, ISO | 0 | 1036.2994 | 7.871% | 81.5681 | 18.78 | 1.198% | 0.22491 | 32.1696 | 51.1745 | 132.7427
SCCT Frame "F" x1, ISO | 0 | 583.7288 | 7.373% | 43.0362 | 13.28 | 0.287% | 0.03811 | 34.4012 | 47.7193 | 90.7555
IC Recips x 6, ISO | 0 | 1572.4256 | 7.871% | 123.7671 | 29.82 | 0.1435% | 0.042787 | 29.6551 | 59.5179 | 183.285
CCCT Dry "G/H", 1x1, ISO | 0 | 1404.8872 | 7.256% | 101.9427 | 20.52 | 0.153% | 0.031405 | 22.792 | 43.3434 | 145.2861
CCCT Dry "G/H", DF, 1x1, ISO | 0 | 443.0343 | 7.256% | 32.1478 | 5.39 | 0% | 0 | 31.7541 | 37.1441 | 69.292
CCCT Dry "G/H", 2x1, ISO | 0 | 1042.9757 | 7.256% | 75.6813 | 13.79 | 0.153% | 0.021105 | 22.7526 | 36.5637 | 112.2451
CCCT Dry "G/H", DF, 2x1, ISO | 0 | 348.0646 | 7.256% | 25.2566 | 4.44 | 0% | 0 | 31.5643 | 36.0043 | 61.2608
CCCT Dry "J/HA.02", 1x1, ISO | 0 | 1226.2066 | 7.256% | 88.9771 | 17.66 | 0.153% | 0.027028 | 22.6273 | 40.3143 | 129.2914
CCCT Dry "J/HA.02", DF, 1x1, ISO | 0 | 378.1246 | 7.256% | 27.4378 | 4.86 | 0% | 0 | 31.8007 | 36.6607 | 64.0985
CCCT Dry, "J/HA.02" 2X1, ISO | 0 | 913.0611 | 7.256% | 66.2543 | 12 | 0.153% | 0.018366 | 22.595 | 34.6134 | 100.8677
CCCT Dry "J/HA.02", DF, 2X1, ISO | 0 | 301.6021 | 7.256% | 21.8851 | 4.05 | 0% | 0 | 31.6287 | 35.6787 | 57.5639
SCCT Aero x3 | 1500 | 1463.5665 | 7.871% | 115.1987 | 27.96 | 1.331% | 0.37206 | 32.843 | 61.1751 | 176.3738
Intercooled SCCT Aero x2 | 1500 | 1097.0774 | 7.871% | 86.352 | 19.88 | 1.198% | 0.23809 | 32.2377 | 52.3558 | 138.7078
SCCT Frame "F" x1 | 1500 | 616.1377 | 7.373% | 45.4256 | 14.02 | 0.287% | 0.040233 | 34.4012 | 48.4614 | 93.887
IC Recips x 6 | 1500 | 1572.4256 | 7.871% | 123.7671 | 29.82 | 0.1435% | 0.042787 | 29.6551 | 59.5179 | 183.285
CCCT Dry "G/H", 1x1 | 1500 | 1484.3381 | 7.256% | 107.7078 | 21.68 | 0.153% | 0.03318 | 22.7885 | 44.5016 | 152.2095
CCCT Dry "G/H", DF, 1x1 | 1500 | 443.0044 | 7.256% | 32.1457 | 5.39 | 0% | 0 | 32.2807 | 37.6707 | 69.8163
CCCT Dry "G/H", 2x1 | 1500 | 1102.2506 | 7.256% | 79.9825 | 14.57 | 0.153% | 0.022299 | 22.7562 | 37.3485 | 117.331
CCCT Dry "G/H", DF, 2x1 | 1500 | 348.0655 | 7.256% | 25.2566 | 4.44 | 0% | 0 | 32.1266 | 36.5666 | 61.8233
CCCT Dry "J/HA.02", 1x1 | 1500 | 1296.7314 | 7.256% | 94.0946 | 18.67 | 0.153% | 0.028574 | 22.6273 | 41.3258 | 135.4204
CCCT Dry "J/HA.02", DF, 1x1 | 1500 | 378.1 | 7.256% | 27.436 | 4.86 | 0% | 0 | 32.363 | 37.223 | 64.6591
CCCT Dry, "J/HA.02" 2X1 | 1500 | 965.2047 | 7.256% | 70.038 | 12.69 | 0.153% | 0.019422 | 22.5807 | 35.2901 | 105.3282
CCCT Dry "J/HA.02", DF, 2X1 | 1500 | 301.5809 | 7.256% | 21.8836 | 4.05 | 0% | 0 | 31.901 | 35.951 | 57.8345
SCCT Aero x3 | 3000 | 1548.2276 | 7.871% | 121.8625 | 29.58 | 1.331% | 0.39362 | 16.8477 | 46.8213 | 168.6838
Intercooled SCCT Aero x2 | 3000 | 1164.1529 | 7.871% | 91.6316 | 21.1 | 1.198% | 0.2527 | 16.5413 | 37.894 | 129.5256
SCCT Frame "F" x1 | 3000 | 650.5821 | 7.373% | 47.965 | 14.81 | 0.287% | 0.0425 | 17.6329 | 32.4854 | 80.4504
IC Recips x 6 | 3000 | 1572.4256 | 7.871% | 123.7671 | 29.82 | 0.1435% | 0.042787 | 15.1891 | 45.0519 | 168.8191
CCCT Dry "G/H", 1x1 | 3000 | 1569.1214 | 7.256% | 113.86 | 22.92 | 0.153% | 0.035078 | 11.6794 | 34.6345 | 148.4945
CCCT Dry "G/H", DF, 1x1 | 3000 | 443.0253 | 7.256% | 32.1472 | 5.39 | 0% | 0 | 16.6128 | 22.0028 | 54.15
CCCT Dry "G/H", 2x1 | 3000 | 1164.2775 | 7.256% | 84.4833 | 15.39 | 0.153% | 0.023554 | 11.6538 | 27.0673 | 111.5506
CCCT Dry "G/H", DF, 2x1 | 3000 | 348.2264 | 7.256% | 25.2683 | 4.44 | 0% | 0 | 16.534 | 20.974 | 46.2423
CCCT Dry "J/HA.02", 1x1 | 3000 | 1370.4877 | 7.256% | 99.4465 | 19.73 | 0.153% | 0.030196 | 11.5969 | 31.3571 | 130.8036
CCCT Dry "J/HA.02", DF, 1x1 | 3000 | 378.1374 | 7.256% | 27.4387 | 4.86 | 0% | 0 | 16.6716 | 21.5316 | 48.9703
CCCT Dry, "J/HA.02" 2X1 | 3000 | 1020.1188 | 7.256% | 74.0228 | 13.41 | 0.153% | 0.020524 | 11.573 | 25.0036 | 99.0263
CCCT Dry "J/HA.02", DF, 2X1 | 3000 | 301.591 | 7.256% | 21.8843 | 4.05 | 0% | 0 | 16.5835 | 20.6335 | 42.5178
|  | Capital Cost $/kW |  |  | Fixed Cost
Supply Side Resource Options Mid-Calendar Year 2016 Dollars ($) |  |  |  |  | Fixed O&M $/kW-Yr
Resource Description | Elevation (AFSL) | Total Capital Cost | Payment Factor | Annual Payment ($/kW-Yr) | O&M | Capitalized Premium | O&M Capitalized | Gas Transportation | Total | Total Fixed ($/kW-Yr)
SCCT Aero x3 | 5050 | 1667.9175 | 7.871% | 131.2834 | 31.86 | 1.331% | 0.42396 | 13.9942 | 46.2781 | 177.5615
Intercooled SCCT Aero x2 | 5050 | 1259.0673 | 7.871% | 99.1024 | 22.82 | 1.198% | 0.2733 | 13.7551 | 36.8484 | 135.9508
SCCT Frame "F" x1 | 5050 | 701.5991 | 7.373% | 51.7263 | 15.97 | 0.287% | 0.045829 | 14.6414 | 30.6572 | 82.3836
IC Recips x 6 | 5050 | 1572.4256 | 7.871% | 123.7671 | 29.82 | 0.1435% | 0.042787 | 12.619 | 42.4818 | 166.2489
CCCT Dry "G/H", 1x1 | 5050 | 1693.3409 | 7.256% | 122.8737 | 24.74 | 0.153% | 0.037864 | 9.7071 | 34.485 | 157.3587
CCCT Dry "G/H", DF, 1x1 | 5050 | 442.8693 | 7.256% | 32.1359 | 5.39 | 0% | 0 | 13.9683 | 19.3583 | 51.4941
CCCT Dry "G/H", 2x1 | 5050 | 1257.4204 | 7.256% | 91.242 | 16.63 | 0.153% | 0.025452 | 9.6934 | 26.3489 | 117.5909
CCCT Dry "G/H", DF, 2x1 | 5050 | 348.0331 | 7.256% | 25.2543 | 4.44 | 0% | 0 | 13.9211 | 18.3611 | 43.6153
CCCT Dry "J/HA.02", 1x1 | 5050 | 1476.6324 | 7.256% | 107.1487 | 21.26 | 0.153% | 0.032538 | 9.634 | 30.9266 | 138.0753
CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 378.0723 | 7.256% | 27.434 | 4.86 | 0% | 0 | 14.0277 | 18.8877 | 46.3217
CCCT Dry, "J/HA.02" 2X1 | 5050 | 1099.6822 | 7.256% | 79.7961 | 14.45 | 0.153% | 0.022115 | 9.6203 | 24.0924 | 103.8885
CCCT Dry "J/HA.02", DF, 2X1 | 5050 | 301.5804 | 7.256% | 21.8835 | 4.05 | 0% | 0 | 13.947 | 17.997 | 39.8805
SCCT Aero x3 | 6500 | 1809.4081 | 7.871% | 142.4203 | 34.56 | 1.331% | 0.45989 | 9.1121 | 44.132 | 186.5522
Intercooled SCCT Aero x2 | 6500 | 1324.1743 | 7.871% | 104.227 | 24 | 1.198% | 0.28743 | 8.9218 | 33.2092 | 137.4363
SCCT Frame "F" x1 | 6500 | 738.8661 | 7.373% | 54.4739 | 16.81 | 0.287% | 0.04824 | 9.5184 | 26.3766 | 80.8505
IC Recips x 6 | 6500 | 1637.0477 | 7.871% | 128.8536 | 31.04 | 0.1435% | 0.044538 | 8.3015 | 39.386 | 168.2396
CCCT Dry "G/H", 1x1 | 6500 | 1793.4362 | 7.256% | 130.1369 | 26.2 | 0.153% | 0.040098 | 6.3373 | 32.5774 | 162.7143
CCCT Dry "G/H", DF, 1x1 | 6500 | 442.9914 | 7.256% | 32.1447 | 5.39 | 0% | 0 | 9.4381 | 14.8281 | 46.9728
CCCT Dry "G/H", 2x1 | 6500 | 1331.6368 | 7.256% | 96.6274 | 17.61 | 0.153% | 0.026951 | 6.3274 | 23.9644 | 120.5918
CCCT Dry "G/H", DF, 2x1 | 6500 | 347.9768 | 7.256% | 25.2502 | 4.44 | 0% | 0 | 9.3757 | 13.8157 | 39.0659
CCCT Dry "J/HA.02", 1x1 | 6500 | 1550.928 | 7.256% | 112.5398 | 22.33 | 0.153% | 0.034175 | 6.2789 | 28.643 | 141.1828
CCCT Dry "J/HA.02", DF, 1x1 | 6500 | 378.0653 | 7.256% | 27.4335 | 4.86 | 0% | 0 | 9.4381 | 14.2981 | 41.7316
CCCT Dry, "J/HA.02" 2X1 | 6500 | 1155.0631 | 7.256% | 83.8147 | 15.18 | 0.153% | 0.023232 | 6.2699 | 21.4732 | 105.2879
CCCT Dry "J/HA.02", DF, 2X1 | 6500 | 301.7457 | 7.256% | 21.8955 | 4.06 | 0% | 0 | 9.3836 | 13.4436 | 35.3391
SCPC with CCS | 4500 | 6077.664 | 7.157% | 434.9807 | 69.2162 | 0% | 0 | 0 | 69.2162 | 504.1969
IGCC with CCS | 4500 | 5884.4667 | 6.853% | 403.2856 | 55.7752 | 0% | 0 | 0 | 55.7752 | 459.0608
PC CCS retrofit @ 500 MW | 4500 | 1334.3443 | 7.157% | 95.4995 | 74.5171 | 0% | 0 | 0 | 74.5171 | 170.0166
SCPC with CCS | 6500 | 6882.6526 | 7.157% | 492.594 | 64.2924 | 0% | 0 | 0 | 64.2924 | 556.8864
IGCC with CCS | 6500 | 6663.0057 | 6.853% | 456.6419 | 60.7619 | 0% | 0 | 0 | 60.7619 | 517.4038
PC CCS retrofit @ 500 MW | 6500 | 1511.0786 | 7.135% | 107.821 | 69.2162 | 0% | 0 | 0 | 69.2162 | 177.0372
|  | Capital Cost $/kW |  |  | Fixed Cost
Supply Side Resource Options Mid-Calendar Year 2016 Dollars ($) |  |  |  |  | Fixed O&M $/kW-Yr
Resource Description | Elevation (AFSL) | Total Capital Cost | Payment Factor | Annual Payment ($/kW-Yr) | O&M | Capitalized Premium | O&M Capitalized | Gas Transportation | Total | Total Fixed ($/kW-Yr)
Blundell Dual Flash 90% CF | 4500 | 6130.8225 | 6.311% | 386.9416 | 100.51 | 0.9183% | 0.92296 | 0 | 101.433 | 488.3745
Greenfield Binary 90% CF | 4500 | 6793.2297 | 6.311% | 428.7488 | 100.5063 | 0.9183% | 0.92293 | 0 | 101.4292 | 530.1781
Generic Geothermal PPA 90% CF | 4500 | 0 | 6.311% | 0 | 0 | 0% | 0 | 0 | 0 | 0
2.0 MW turbine 38% CF WA,2021 | 1500 | 1799.7506 | 7.067% | 127.1971 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 164.7627
2.0 MW turbine 38% CF OR, 2021 | 1500 | 1773.9008 | 7.067% | 125.3702 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 162.9358
2.0 MW turbine 38% CF ID, 2021 | 4500 | 1811.0329 | 7.067% | 127.9945 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 165.5601
2.0 MW turbine 31% CF UT, 2021 | 4500 | 1735.3716 | 7.067% | 122.6471 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 160.2127
3.3 MW turbine 43% CF WY, 2021 | 6500 | 1737.2477 | 7.067% | 122.7797 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 160.3453
2.0 MW turbine 38% CF WA,2024 | 1500 | 1799.7506 | 7.067% | 127.1971 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 164.7627
2.0 MW turbine 38% CF OR, 2024 | 1500 | 1773.9008 | 7.067% | 125.3702 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 162.9358
2.0 MW turbine 38% CF ID, 2024 | 4500 | 1811.0329 | 7.067% | 127.9945 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 165.5601
2.0 MW turbine 31% CF UT, 2024 | 4500 | 1735.3716 | 7.067% | 122.6471 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 160.2127
3.3 MW turbine 43% CF WY, 2024 | 6500 | 1737.2477 | 7.067% | 122.7797 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 160.3453
PV Poly-Si Fixed Tilt 26.8% AC CF (1.35 MWdc/Mwac) UT, 2019 | 4500 | 1723.7488 | 7.716% | 132.9989 | 18.45 | 1.461% | 0.26953 | 0 | 18.7195 | 151.7184
PV Poly-Si Single Tracking 31.1% AC CF (1.25 MWdc/Mwac) UT, 2019 | 4500 | 1822.4072 | 7.716% | 140.6111 | 19.41 | 1.461% | 0.28356 | 0 | 19.6936 | 160.3046
PV Poly-Si Fixed Tilt 24.9% AC CF (1.35 MWdc/Mwac) OR, 2019 | 4800 | 1761.8948 | 7.716% | 135.9421 | 18.47 | 1.461% | 0.26983 | 0 | 18.7398 | 154.682
PV Poly-Si Single Tracking 28.8% AC CF (1.25 MWdc/Mwac) OR, 2019 | 4800 | 1856.7386 | 7.716% | 143.26 | 19.44 | 1.461% | 0.284 | 0 | 19.724 | 162.984
PV Poly-Si Fixed Tilt 26.8% AC CF (1.35 MWdc/Mwac) UT, 2023 | 4500 | 1723.7488 | 7.716% | 132.9989 | 18.45 | 1.461% | 0.26953 | 0 | 18.7195 | 151.7184
PV Poly-Si Single Tracking 31.1% AC CF (1.25 MWdc/Mwac) UT, 2023 | 4500 | 1822.4072 | 7.716% | 140.6111 | 19.41 | 1.461% | 0.28356 | 0 | 19.6936 | 160.3046
PV Poly-Si Fixed Tilt 24.9% AC CF (1.35 MWdc/Mwac) OR, 2023 | 4800 | 1761.8948 | 7.716% | 135.9421 | 18.47 | 1.461% | 0.26983 | 0 | 18.7398 | 154.682
PV Poly-Si Single Tracking 28.8% AC CF (1.25 MWdc/Mwac) OR, 2023 | 4800 | 1856.7386 | 7.716% | 143.26 | 19.44 | 1.461% | 0.284 | 0 | 19.724 | 162.984
CSP Trough w Natural Gas | 4500 | 6447.5397 | 7.067% | 455.679 | 68.4642 | 0% | 0 | 17.8995 | 86.3638 | 542.0427
CSP Tower 24% CF | 4500 | 6141.4654 | 7.067% | 434.0472 | 68.4642 | 0% | 0 | 0 | 68.4642 | 502.5114
CSP Tower Molten Salt 30% CF | 4500 | 7367.0328 | 7.067% | 520.664 | 68.4642 | 0% | 0 | 0 | 68.4642 | 589.1282
Forestry Byproduct | 1500 | 4383.3025 | 7.067% | 309.7893 | 42.04 | 0% | 0 | 0 | 42.04 | 351.8293
Pumped Storage 1 (3,800 MWh) | 4457 | 3468.3873 | 6.517% | 226.047 | 21.1 | 0% | 0 | 0 | 21.1 | 247.147
Pumped Storage 2 (12,000 MWh) | 580 | 3600.6916 | 6.517% | 234.6697 | 15.58 | 0% | 0 | 0 | 15.58 | 250.2497
Pumped Storage 3 (7,000 MWh) | 6359 | 2860.7143 | 6.517% | 186.4428 | 16.86 | 0% | 0 | 0 | 16.86 | 203.3028
CAES (15,360 MWh) | 4640 | 2138.2486 | 7.871% | 168.3036 | 18.9 | 0% | 0 | 0 | 18.9 | 187.2036
Advanced Fission | 5000 | 6524.1573 | 7.018% | 457.8859 | 98.35 | 5.816% | 5.7198 | 0 | 104.0698 | 561.9557
Small Modular Reactor x 12 | 5000 | 9675.8543 | 7.018% | 679.082 | 167.77 | 11.48% | 19.2574 | 0 | 187.0274 | 866.1094
|  | Capital Cost $/kW |  |  | Fixed Cost
Supply Side Resource Options Mid-Calendar Year 2016 Dollars ($) |  |  |  |  | Fixed O&M $/kW-Yr
Resource Description | Elevation (AFSL) | Total Capital Cost | Payment Factor | Annual Payment ($/kW-Yr) | O&M | Capitalized Premium | O&M Capitalized | Gas Transportation | Total | Total Fixed ($/kW-Yr)
Brownfield Site
Dave Johnston
SCCT Aero x3 | 5050 | 1482.6307 | 7.871% | 116.6993 | 31.86 | 1.331% | 0.42396 | 53.2245 | 85.5085 | 202.2078
Intercooled SCCT Aero x2 | 5050 | 1135.8112 | 7.871% | 89.4008 | 22.82 | 1.198% | 0.2733 | 52.3151 | 75.4084 | 164.8092
SCCT Frame "F" x1 | 5050 | 589.4961 | 7.373% | 43.4614 | 15.97 | 0.287% | 0.045829 | 55.6862 | 71.702 | 115.1634
IC Recips x 6 | 5050 | 1369.8564 | 7.871% | 107.8227 | 29.82 | 0.1435% | 0.042787 | 47.9942 | 77.8569 | 185.6797
CCCT Dry "G/H", 1x1 | 5050 | 1519.0366 | 7.256% | 110.2257 | 24.74 | 0.153% | 0.037864 | 36.9195 | 61.6973 | 171.923
CCCT Dry "G/H", DF, 1x1 | 5050 | 397.2825 | 7.256% | 28.828 | 5.39 | 0% | 0 | 53.126 | 58.516 | 87.344
CCCT Dry "J/HA.02", 1x1 | 5050 | 1334.21 | 7.256% | 96.8141 | 21.26 | 0.153% | 0.032538 | 36.6414 | 57.934 | 154.7481
CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 341.6069 | 7.256% | 24.788 | 4.86 | 0% | 0 | 53.3519 | 58.2119 | 82.9999
Hunter
SCCT Aero x3 | 5050 | 1482.6307 | 7.871% | 116.6993 | 31.86 | 1.331% | 0.42396 | 13.9942 | 46.2781 | 162.9774
Intercooled SCCT Aero x2 | 5050 | 1135.8112 | 7.871% | 89.4008 | 22.82 | 1.198% | 0.2733 | 13.7551 | 36.8484 | 126.2492
SCCT Frame "F" x1 | 5050 | 589.4961 | 7.373% | 43.4614 | 15.97 | 0.287% | 0.045829 | 14.6414 | 30.6572 | 74.1186
IC Recips x 6 | 5050 | 1369.8564 | 7.871% | 107.8227 | 29.82 | 0.1435% | 0.042787 | 12.619 | 42.4818 | 150.3045
CCCT Dry "G/H", 1x1 | 5050 | 1519.0366 | 7.256% | 110.2257 | 24.74 | 0.153% | 0.037864 | 9.7071 | 34.485 | 144.7107
CCCT Dry "G/H", DF, 1x1 | 5050 | 397.2825 | 7.256% | 28.828 | 5.39 | 0% | 0 | 13.9683 | 19.3583 | 48.1862
CCCT Dry "J/HA.02", 1x1 | 5050 | 1334.21 | 7.256% | 96.8141 | 21.26 | 0.153% | 0.032538 | 9.634 | 30.9266 | 127.7407
CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 341.6069 | 7.256% | 24.788 | 4.86 | 0% | 0 | 14.0277 | 18.8877 | 43.6757
Huntington
SCCT Aero x3 | 5050 | 1482.6307 | 7.871% | 116.6993 | 31.86 | 1.331% | 0.42396 | 13.9942 | 46.2781 | 162.9774
Intercooled SCCT Aero x2 | 5050 | 1135.8112 | 7.871% | 89.4008 | 22.82 | 1.198% | 0.2733 | 13.7551 | 36.8484 | 126.2492
SCCT Frame "F" x1 | 5050 | 589.4961 | 7.373% | 43.4614 | 15.97 | 0.287% | 0.045829 | 14.6414 | 30.6572 | 74.1186
IC Recips x 6 | 5050 | 1369.8564 | 7.871% | 107.8227 | 29.82 | 0.1435% | 0.042787 | 12.619 | 42.4818 | 150.3045
CCCT Dry "G/H", 1x1 | 5050 | 1519.0366 | 7.256% | 110.2257 | 24.74 | 0.153% | 0.037864 | 9.7071 | 34.485 | 144.7107
CCCT Dry "G/H", DF, 1x1 | 5050 | 397.2825 | 7.256% | 28.828 | 5.39 | 0% | 0 | 13.9683 | 19.3583 | 48.1862
CCCT Dry "G/H", 2x1 | 5050 | 1163.2405 | 7.256% | 84.4081 | 16.63 | 0.153% | 0.025452 | 9.6934 | 26.3489 | 110.757
CCCT Dry "G/H", DF, 2x1 | 5050 | 321.9656 | 7.256% | 23.3628 | 4.44 | 0% | 0 | 13.9211 | 18.3611 | 41.7238
CCCT Dry "J/HA.02", 1x1 | 5050 | 1334.21 | 7.256% | 96.8141 | 21.26 | 0.153% | 0.032538 | 9.634 | 30.9266 | 127.7407
CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 341.6069 | 7.256% | 24.788 | 4.86 | 0% | 0 | 14.0277 | 18.8877 | 43.6757
|  | Capital Cost $/kW |  |  | Fixed Cost
Supply Side Resource Options Mid-Calendar Year 2016 Dollars ($) |  |  |  |  | Fixed O&M $/kW-Yr
Resource Description | Elevation (AFSL) | Total Capital Cost | Payment Factor | Annual Payment ($/kW-Yr) | O&M | Capitalized Premium | O&M Capitalized | Gas Transportation | Total | Total Fixed ($/kW-Yr)
Jim Bridger
SCCT Aero x3 | 6500 | 1608.4033 | 7.871% | 126.599 | 34.56 | 1.331% | 0.45989 | 9.1121 | 44.132 | 170.7309
Intercooled SCCT Aero x2 | 6500 | 1194.5446 | 7.871% | 94.0238 | 24 | 1.198% | 0.28743 | 8.9218 | 33.2092 | 127.233
SCCT Frame "F" x1 | 6500 | 620.8085 | 7.373% | 45.7699 | 16.81 | 0.287% | 0.04824 | 9.5184 | 26.3766 | 72.1465
IC Recips x 6 | 6500 | 1426.1534 | 7.871% | 112.2539 | 31.04 | 0.1435% | 0.044538 | 8.3015 | 39.386 | 151.6399
CCCT Dry "G/H", 1x1 | 6500 | 1608.8286 | 7.256% | 116.7412 | 26.2 | 0.153% | 0.040098 | 6.3373 | 32.5774 | 149.3187
CCCT Dry "G/H", DF, 1x1 | 6500 | 397.392 | 7.256% | 28.8359 | 5.39 | 0% | 0 | 9.4381 | 14.8281 | 43.664
CCCT Dry "J/HA.02", 1x1 | 6500 | 1401.3397 | 7.256% | 101.6852 | 22.33 | 0.153% | 0.034175 | 6.2789 | 28.643 | 130.3283
CCCT Dry "J/HA.02", DF, 1x1 | 6500 | 341.6006 | 7.256% | 24.7875 | 4.86 | 0% | 0 | 9.4381 | 14.2981 | 39.0856
Naughton
SCCT Aero x3 | 6500 | 1608.4033 | 7.871% | 126.599 | 34.56 | 1.331% | 0.45989 | 14.0033 | 49.0232 | 175.6222
Intercooled SCCT Aero x2 | 6500 | 1194.5446 | 7.871% | 94.0238 | 24 | 1.198% | 0.28743 | 13.7109 | 37.9983 | 132.0221
SCCT Frame "F" x1 | 6500 | 620.8085 | 7.373% | 45.7699 | 16.81 | 0.287% | 0.04824 | 14.6277 | 31.4859 | 77.2559
IC Recips x 6 | 6500 | 1426.1534 | 7.871% | 112.2539 | 31.04 | 0.1435% | 0.044538 | 12.7576 | 43.8421 | 156.096
CCCT Dry "J/HA.02", 1x1 | 6500 | 1401.3397 | 7.256% | 101.6852 | 22.33 | 0.153% | 0.034175 | 9.6493 | 32.0134 | 133.6987
CCCT Dry "J/HA.02", DF, 1x1 | 6500 | 341.6006 | 7.256% | 24.7875 | 4.86 | 0% | 0 | 14.5043 | 19.3643 | 44.1519
Wyodak
SCCT Aero x3 | 6500 | 1608.4033 | 7.871% | 126.599 | 34.56 | 1.331% | 0.45989 | 53.2593 | 88.2792 | 214.8781
Intercooled SCCT Aero x2 | 6500 | 1194.5446 | 7.871% | 94.0238 | 24 | 1.198% | 0.28743 | 52.1472 | 76.4346 | 170.4584
SCCT Frame "F" x1 | 6500 | 620.8085 | 7.373% | 45.7699 | 16.81 | 0.287% | 0.04824 | 55.6341 | 72.4923 | 118.2622
IC Recips x 6 | 6500 | 1426.1534 | 7.871% | 112.2539 | 31.04 | 0.1435% | 0.044538 | 48.5212 | 79.6058 | 191.8597

## Table 6.2 P2
|  | Convert to Mills |  |  |  |  | Variable Costs (mills/kWh) |  |  |  |  | Total Costs and Credits (Mills/kWh)
Supply Side Resource Options Mid-Calendar Year 2016 Dollars ($) | Elevation (AFSL) |  |  |  | Levelized Fuel | [7 empty] | Credits
Resource Description |  | Capacity Factor | Total Fixed (Mills/kWh) | Storage Efficiency | ¢/mmBtu | Mills/kWh | O&M | Capitalized Premium | O&M Capitalized | Integration Cost | Environmental | Total Resource Cost | PTC Tax Credits / ITC (Solar Only) | Total Resource Cost - With PTC / ITC Credits
SCCT Aero x3, ISO | 0 | 33% | 59.597 | na | 294.97 | 27.149 | 7.54 | 12.11% | 0.91304 | 0 | 0 | 95.1991 | 0 | 95.1991
Intercooled SCCT Aero x2, ISO | 0 | 33% | 45.919 | na | 294.97 | 26.4913 | 5.05 | 12.11% | 0.61152 | 0 | 0 | 78.0718 | 0 | 78.0718
SCCT Frame "F" x1, ISO | 0 | 33% | 31.3946 | na | 294.97 | 28.3289 | 5.5 | 13.92% | 0.7655 | 0 | 0 | 65.989 | 0 | 65.989
IC Recips x 6, ISO | 0 | 33% | 63.4029 | na | 294.97 | 24.4206 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 95.9576 | 0 | 95.9576
CCCT Dry "G/H", 1x1, ISO | 0 | 78% | 21.263 | na | 294.97 | 18.7689 | 1.76 | 10.71% | 0.18855 | 0 | 0 | 41.9805 | 0 | 41.9805
CCCT Dry "G/H", DF, 1x1, ISO | 0 | 12% | 65.917 | na | 294.97 | 26.1491 | 0.15 | 0% | 0 | 0 | 0 | 92.2161 | 0 | 92.2161
CCCT Dry "G/H", 2x1, ISO | 0 | 78% | 16.4274 | na | 294.97 | 18.7365 | 1.67 | 11.33% | 0.18913 | 0 | 0 | 37.023 | 0 | 37.023
CCCT Dry "G/H", DF, 2x1, ISO | 0 | 12% | 58.2771 | na | 294.97 | 25.9928 | 0.16 | 0% | 0 | 0 | 0 | 84.4298 | 0 | 84.4298
CCCT Dry "J/HA.02", 1x1, ISO | 0 | 78% | 18.9222 | na | 294.97 | 18.6333 | 1.7 | 10.71% | 0.18213 | 0 | 0 | 39.4375 | 0 | 39.4375
CCCT Dry "J/HA.02", DF, 1x1, ISO | 0 | 12% | 60.9765 | na | 294.97 | 26.1874 | 0.16 | 0% | 0 | 0 | 0 | 87.3239 | 0 | 87.3239
CCCT Dry, "J/HA.02" 2X1, ISO | 0 | 78% | 14.7623 | na | 294.97 | 18.6067 | 1.62 | 11.33% | 0.18347 | 0 | 0 | 35.1725 | 0 | 35.1725
CCCT Dry "J/HA.02", DF, 2X1, ISO | 0 | 12% | 54.7601 | na | 294.97 | 26.0459 | 0.16 | 0% | 0 | 0 | 0 | 80.966 | 0 | 80.966
SCCT Aero x3 | 1500 | 33% | 61.0121 | na | 294.97 | 27.0458 | 7.76 | 12.11% | 0.93968 | 0 | 0 | 96.7576 | 0 | 96.7576
Intercooled SCCT Aero x2 | 1500 | 33% | 47.9825 | na | 294.97 | 26.5473 | 5.35 | 12.11% | 0.64785 | 0 | 0 | 80.5276 | 0 | 80.5276
SCCT Frame "F" x1 | 1500 | 33% | 32.4779 | na | 294.97 | 28.3289 | 5.81 | 13.92% | 0.80864 | 0 | 0 | 67.4254 | 0 | 67.4254
IC Recips x 6 | 1500 | 33% | 63.4029 | na | 294.97 | 24.4206 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 95.9576 | 0 | 95.9576
CCCT Dry "G/H", 1x1 | 1500 | 78% | 22.2763 | na | 294.97 | 18.766 | 1.86 | 10.71% | 0.19927 | 0 | 0 | 43.1016 | 0 | 43.1016
CCCT Dry "G/H", DF, 1x1 | 1500 | 12% | 66.4158 | na | 294.97 | 26.5827 | 0.15 | 0% | 0 | 0 | 0 | 93.1485 | 0 | 93.1485
CCCT Dry "G/H", 2x1 | 1500 | 78% | 17.1717 | na | 294.97 | 18.7394 | 1.77 | 11.33% | 0.20046 | 0 | 0 | 37.8816 | 0 | 37.8816
CCCT Dry "G/H", DF, 2x1 | 1500 | 12% | 58.8121 | na | 294.97 | 26.4559 | 0.16 | 0% | 0 | 0 | 0 | 85.4279 | 0 | 85.4279
CCCT Dry "J/HA.02", 1x1 | 1500 | 78% | 19.8192 | na | 294.97 | 18.6333 | 1.8 | 10.71% | 0.19284 | 0 | 0 | 40.4453 | 0 | 40.4453
CCCT Dry "J/HA.02", DF, 1x1 | 1500 | 12% | 61.5098 | na | 294.97 | 26.6505 | 0.16 | 0% | 0 | 0 | 0 | 88.3203 | 0 | 88.3203
CCCT Dry, "J/HA.02" 2X1 | 1500 | 78% | 15.4151 | na | 294.97 | 18.5949 | 1.71 | 11.33% | 0.19366 | 0 | 0 | 35.9137 | 0 | 35.9137
CCCT Dry "J/HA.02", DF, 2X1 | 1500 | 12% | 55.0176 | na | 294.97 | 26.27 | 0.16 | 0% | 0 | 0 | 0 | 81.4477 | 0 | 81.4477
SCCT Aero x3 | 3000 | 33% | 58.3519 | na | 293.35 | 26.9383 | 8.21 | 12.11% | 0.99417 | 0 | 0 | 94.4944 | 0 | 94.4944
Intercooled SCCT Aero x2 | 3000 | 33% | 44.8061 | na | 293.35 | 26.4484 | 5.67 | 12.11% | 0.6866 | 0 | 0 | 77.6112 | 0 | 77.6112
SCCT Frame "F" x1 | 3000 | 33% | 27.8298 | na | 293.35 | 28.1939 | 6.13 | 13.92% | 0.85318 | 0 | 0 | 63.0069 | 0 | 63.0069
IC Recips x 6 | 3000 | 33% | 58.3987 | na | 293.35 | 24.2864 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 90.8193 | 0 | 90.8193
CCCT Dry "G/H", 1x1 | 3000 | 78% | 21.7326 | na | 293.35 | 18.6747 | 1.97 | 10.71% | 0.21105 | 0 | 0 | 42.5883 | 0 | 42.5883
CCCT Dry "G/H", DF, 1x1 | 3000 | 12% | 51.5126 | na | 293.35 | 26.5628 | 0.15 | 0% | 0 | 0 | 0 | 78.2254 | 0 | 78.2254
CCCT Dry "G/H", 2x1 | 3000 | 78% | 16.3258 | na | 293.35 | 18.6336 | 1.86 | 11.33% | 0.21065 | 0 | 0 | 37.03 | 0 | 37.03
CCCT Dry "G/H", DF, 2x1 | 3000 | 12% | 43.99 | na | 293.35 | 26.4367 | 0.16 | 0% | 0 | 0 | 0 | 70.5867 | 0 | 70.5867
CCCT Dry "J/HA.02", 1x1 | 3000 | 78% | 19.1435 | na | 293.35 | 18.5427 | 1.9 | 10.71% | 0.20355 | 0 | 0 | 39.7897 | 0 | 39.7897
CCCT Dry "J/HA.02", DF, 1x1 | 3000 | 12% | 46.5851 | na | 293.35 | 26.6567 | 0.16 | 0% | 0 | 0 | 0 | 73.4018 | 0 | 73.4018
CCCT Dry, "J/HA.02" 2X1 | 3000 | 78% | 14.4928 | na | 293.35 | 18.5045 | 1.81 | 11.33% | 0.20499 | 0 | 0 | 35.0123 | 0 | 35.0123
CCCT Dry "J/HA.02", DF, 2X1 | 3000 | 12% | 40.4469 | na | 293.35 | 26.5159 | 0.16 | 0% | 0 | 0 | 0 | 67.1228 | 0 | 67.1228
|  | Convert to Mills |  |  |  |  | Variable Costs (mills/kWh) |  |  |  |  | Total Costs and Credits (Mills/kWh)
Supply Side Resource Options Mid-Calendar Year 2016 Dollars ($) | Elevation (AFSL) |  |  |  | Levelized Fuel | [7 empty] | Credits
Resource Description |  | Capacity Factor | Total Fixed (Mills/kWh) | Storage Efficiency | ¢/mmBtu | Mills/kWh | O&M | Capitalized Premium | O&M Capitalized | Integration Cost | Environmental | Total Resource Cost | PTC Tax Credits / ITC (Solar Only) | Total Resource Cost - With PTC / ITC Credits
SCCT Aero x3 | 5050 | 33% | 61.423 | na | 294.97 | 27.1048 | 8.85 | 12.11% | 1.0717 | 0 | 0 | 98.4494 | 0 | 98.4494
Intercooled SCCT Aero x2 | 5050 | 33% | 47.0288 | na | 294.97 | 26.6417 | 6.14 | 12.11% | 0.74351 | 0 | 0 | 80.554 | 0 | 80.554
SCCT Frame "F" x1 | 5050 | 33% | 28.4985 | na | 294.97 | 28.3584 | 6.61 | 13.92% | 0.91999 | 0 | 0 | 64.3869 | 0 | 64.3869
IC Recips x 6 | 5050 | 33% | 57.5096 | na | 294.97 | 24.4412 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 90.085 | 0 | 90.085
CCCT Dry "G/H", 1x1 | 5050 | 78% | 23.0299 | na | 294.97 | 18.8014 | 2.12 | 10.71% | 0.22712 | 0 | 0 | 44.1784 | 0 | 44.1784
CCCT Dry "G/H", DF, 1x1 | 5050 | 12% | 48.9861 | na | 294.97 | 27.0546 | 0.15 | 0% | 0 | 0 | 0 | 76.1907 | 0 | 76.1907
CCCT Dry "G/H", 2x1 | 5050 | 78% | 17.2098 | na | 294.97 | 18.7748 | 2.01 | 11.33% | 0.22764 | 0 | 0 | 38.2223 | 0 | 38.2223
CCCT Dry "G/H", DF, 2x1 | 5050 | 12% | 41.491 | na | 294.97 | 26.9632 | 0.16 | 0% | 0 | 0 | 0 | 68.6142 | 0 | 68.6142
CCCT Dry "J/HA.02", 1x1 | 5050 | 78% | 20.2077 | na | 294.97 | 18.6598 | 2.05 | 10.71% | 0.21962 | 0 | 0 | 41.1371 | 0 | 41.1371
CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 12% | 44.0655 | na | 294.97 | 27.1697 | 0.16 | 0% | 0 | 0 | 0 | 71.3952 | 0 | 71.3952
CCCT Dry, "J/HA.02" 2X1 | 5050 | 78% | 15.2044 | na | 294.97 | 18.6333 | 1.95 | 11.33% | 0.22085 | 0 | 0 | 36.0085 | 0 | 36.0085
CCCT Dry "J/HA.02", DF, 2X1 | 5050 | 12% | 37.9381 | na | 294.97 | 27.0134 | 0.16 | 0% | 0 | 0 | 0 | 65.1114 | 0 | 65.1114
SCCT Aero x3 | 6500 | 33% | 64.5331 | na | 289.01 | 26.5745 | 9.6 | 12.11% | 1.1625 | 0 | 0 | 101.87 | 0 | 101.87
Intercooled SCCT Aero x2 | 6500 | 33% | 47.5426 | na | 289.01 | 26.0196 | 6.45 | 12.11% | 0.78105 | 0 | 0 | 80.7933 | 0 | 80.7933
SCCT Frame "F" x1 | 6500 | 33% | 27.9682 | na | 289.01 | 27.7594 | 6.96 | 13.92% | 0.9687 | 0 | 0 | 63.6563 | 0 | 63.6563
IC Recips x 6 | 6500 | 33% | 58.1983 | na | 289.01 | 24.2104 | 7.75 | 9.183% | 0.71169 | 0 | 0 | 90.8703 | 0 | 90.8703
CCCT Dry "G/H", 1x1 | 6500 | 78% | 23.8137 | na | 289.01 | 18.4822 | 2.25 | 10.71% | 0.24105 | 0 | 0 | 44.7869 | 0 | 44.7869
CCCT Dry "G/H", DF, 1x1 | 6500 | 12% | 44.685 | na | 289.01 | 27.5253 | 0.15 | 0% | 0 | 0 | 0 | 72.3603 | 0 | 72.3603
CCCT Dry "G/H", 2x1 | 6500 | 78% | 17.649 | na | 289.01 | 18.4533 | 2.13 | 11.33% | 0.24123 | 0 | 0 | 38.4735 | 0 | 38.4735
CCCT Dry "G/H", DF, 2x1 | 6500 | 12% | 37.1631 | na | 289.01 | 27.3432 | 0.16 | 0% | 0 | 0 | 0 | 64.6664 | 0 | 64.6664
CCCT Dry "J/HA.02", 1x1 | 6500 | 78% | 20.6625 | na | 289.01 | 18.3117 | 2.15 | 10.71% | 0.23033 | 0 | 0 | 41.3545 | 0 | 41.3545
CCCT Dry "J/HA.02", DF, 1x1 | 6500 | 12% | 39.699 | na | 289.01 | 27.5253 | 0.16 | 0% | 0 | 0 | 0 | 67.3843 | 0 | 67.3843
CCCT Dry, "J/HA.02" 2X1 | 6500 | 78% | 15.4092 | na | 289.01 | 18.2857 | 2.05 | 11.33% | 0.23217 | 0 | 0 | 35.977 | 0 | 35.977
CCCT Dry "J/HA.02", DF, 2X1 | 6500 | 12% | 33.6179 | na | 289.01 | 27.3664 | 0.16 | 0% | 0 | 0 | 0 | 61.1443 | 0 | 61.1443
SCPC with CCS | 4500 | 90.25% | 63.7748 | na | 0 | 0 | 6.71 | 0% | 0 | 0 | 0 | NC | 0 | NC
IGCC with CCS | 4500 | 85.56% | 61.2485 | na | 0 | 0 | 11.28 | 0% | 0 | 0 | 0 | NC | 0 | NC
PC CCS retrofit @ 500 MW | 4500 | 90.25% | 21.505 | na | 0 | 0 | 6.2017 | 0% | 0 | 0 | 0 | NC | 0 | NC
SCPC with CCS | 6500 | 90.25% | 70.4393 | na | 0 | 0 | 7.26 | 0% | 0 | 0 | 0 | NC | 0 | NC
IGCC with CCS | 6500 | 85.56% | 69.0327 | na | 0 | 0 | 13.52 | 0% | 0 | 0 | 0 | NC | 0 | NC
PC CCS retrofit @ 500 MW | 6500 | 90.25% | 22.3931 | na | 0 | 0 | 6.71 | 0% | 0 | 0 | 0 | NC | 0 | NC
|  | Convert to Mills |  |  |  |  | Variable Costs (mills/kWh) |  |  |  |  | Total Costs and Credits (Mills/kWh)
Supply Side Resource Options Mid-Calendar Year 2016 Dollars ($) | Elevation (AFSL) |  |  |  | Levelized Fuel | [7 empty] | Credits
Resource Description |  | Capacity Factor | Total Fixed (Mills/kWh) | Storage Efficiency | ¢/mmBtu | Mills/kWh | O&M | Capitalized Premium | O&M Capitalized | Integration Cost | Environmental | Total Resource Cost | PTC Tax Credits / ITC (Solar Only) | Total Resource Cost - With PTC / ITC Credits
Blundell Dual Flash 90% CF | 4500 | 90.25% | 61.7734 | na | 0 | 0 | 1.12 | 0% | 0 | 0 | 0 | 62.8934 | -19.9842 | 42.9092
Greenfield Binary 90% CF | 4500 | 90.25% | 67.0611 | na | 0 | 0 | 1.1246 | 0% | 0 | 0 | 0 | 68.1857 | -19.9842 | 48.2015
Generic Geothermal PPA 90% CF | 4500 | 90.25% | 0 | na | 0 | 0 | 77.34 | 0% | 0 | 0 | 0 | 77.34 | 0 | 77.34
2.0 MW turbine 38% CF WA,2021 | 1500 | 35% | 53.7387 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 54.3117 | -19.9842 | 34.3274
2.0 MW turbine 38% CF OR, 2021 | 1500 | 35% | 53.1428 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 53.7158 | -19.9842 | 33.7316
2.0 MW turbine 38% CF ID, 2021 | 4500 | 35% | 53.9987 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 54.5717 | -19.9842 | 34.5875
2.0 MW turbine 31% CF UT, 2021 | 4500 | 31% | 58.9972 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 59.5702 | -19.9842 | 39.586
3.3 MW turbine 43% CF WY, 2021 | 6500 | 43% | 42.568 | na | 0 | 0 | 0.65 | 0% | 0 | 0.573 | 0 | 43.791 | -19.9842 | 23.8068
2.0 MW turbine 38% CF WA,2024 | 1500 | 38% | 49.4961 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 50.0691 | -7.9937 | 42.0754
2.0 MW turbine 38% CF OR, 2024 | 1500 | 38% | 48.9473 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 49.5203 | -7.9937 | 41.5266
2.0 MW turbine 38% CF ID, 2024 | 4500 | 38% | 49.7357 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 50.3087 | -7.9937 | 42.315
2.0 MW turbine 31% CF UT, 2024 | 4500 | 31% | 58.9972 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 59.5702 | -7.9937 | 51.5765
3.3 MW turbine 43% CF WY, 2024 | 6500 | 43% | 42.568 | na | 0 | 0 | 0.65 | 0% | 0 | 0.573 | 0 | 43.791 | -7.9937 | 35.7974
PV Poly-Si Fixed Tilt 26.8% AC CF (1.35 MWdc/Mwac) UT, 2019 | 4500 | 26.8% | 64.6248 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 65.2278 | -8.84 | 56.3879
PV Poly-Si Single Tracking 31.1% AC CF (1.25 MWdc/Mwac) UT, 2019 | 4500 | 31.1% | 58.8412 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 59.4442 | -8.0537 | 51.3905
PV Poly-Si Fixed Tilt 24.9% AC CF (1.35 MWdc/Mwac) OR, 2019 | 4800 | 24.9% | 70.9147 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 71.5177 | -9.7251 | 61.7926
PV Poly-Si Single Tracking 28.8% AC CF (1.25 MWdc/Mwac) OR, 2019 | 4800 | 28.8% | 64.6023 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 65.2053 | -8.8608 | 56.3446
PV Poly-Si Fixed Tilt 26.8% AC CF (1.35 MWdc/Mwac) UT, 2023 | 4500 | 26.8% | 64.6248 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 65.2278 | -5.9119 | 59.316
PV Poly-Si Single Tracking 31.1% AC CF (1.25 MWdc/Mwac) UT, 2023 | 4500 | 31.1% | 58.8412 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 59.4442 | -5.386 | 54.0582
PV Poly-Si Fixed Tilt 24.9% AC CF (1.35 MWdc/Mwac) OR, 2023 | 4800 | 24.9% | 70.9147 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 71.5177 | -6.5038 | 65.0139
PV Poly-Si Single Tracking 28.8% AC CF (1.25 MWdc/Mwac) OR, 2023 | 4800 | 28.8% | 64.6023 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 65.2053 | -5.9258 | 59.2796
CSP Trough w Natural Gas | 4500 | 33% | 187.5061 | na | 293.96 | 7.3669 | 0 | 0% | 0 | 0.603 | 0 | 195.476 | -8.5882 | 186.8879
CSP Tower 24% CF | 4500 | 24% | 239.018 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 239.621 | -11.2481 | 228.3728
CSP Tower Molten Salt 30% CF | 4500 | 30% | 224.1736 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 224.7766 | -10.7942 | 213.9824
Forestry Byproduct | 1500 | 91% | 44.1353 | na | 0 | 0 | 0.99 | 0% | 0 | 0 | 0 | NC | 0 | NC
Pumped Storage 1 (3,800 MWh) | 4457 | 40.26% | 70.0814 | 77% | 293.35 | 24.0318 | 0 | 0% | 0 | 0 | 0 | 94.1132 | 0 | 94.1132
Pumped Storage 2 (12,000 MWh) | 580 | 41.67% | 68.5616 | 77% | 289.01 | 23.6763 | 0 | 0% | 0 | 0 | 0 | 92.2379 | 0 | 92.2379
Pumped Storage 3 (7,000 MWh) | 6359 | 41.67% | 55.6994 | 77% | 294.97 | 24.1646 | 0 | 0% | 0 | 0 | 0 | 79.8639 | 0 | 79.8639
CAES (15,360 MWh) | 4640 | 30% | 71.2343 | 50% | 294.97 | 24.9368 | 0.77 | 5.456% | 0.04201 | 0 | 0 | 96.983 | 0 | 96.983
Advanced Fission | 5000 | 85.56% | 74.975 | na | 0 | 0 | 11.37 | 0% | 0 | 0 | 0 | 86.345 | 0 | 86.345
Small Modular Reactor x 12 | 5000 | 85.56% | 115.5546 | na | 0 | 0 | 15 | 0% | 0 | 0 | 0 | 130.5546 | 0 | 130.5546
| Elevation (AFSL) | Convert to Mills |  |  |  |  | Variable Costs (mills/kWh) |  |  |  |  | Total Costs and Credits (Mills/kWh)
Supply Side Resource Options Mid-Calendar Year 2016 Dollars ($) |  |  |  |  | Levelized Fuel | [7 empty] | Credits
Resource Description |  | Capacity Factor | Total Fixed (Mills/kWh) | Storage Efficiency | ¢/mmBtu | Mills/kWh | O&M | Capitalized Premium | O&M Capitalized | Integration Cost | Environmental | Total Resource Cost | PTC Tax Credits / ITC (Solar Only) | Total Resource Cost - With PTC / ITC Credits
Brownfield Site
Dave Johnston
SCCT Aero x3 | 5050 | 33% | 69.9487 | na | 289.04 | 26.5599 | 8.85 | 12.11% | 1.0717 | 0 | 0 | 106.4303 | 0 | 106.4303
Intercooled SCCT Aero x2 | 5050 | 33% | 57.0116 | na | 289.04 | 26.1061 | 6.14 | 12.11% | 0.74351 | 0 | 0 | 90.0012 | 0 | 90.0012
SCCT Frame "F" x1 | 5050 | 33% | 39.8379 | na | 289.04 | 27.7883 | 6.61 | 13.92% | 0.91999 | 0 | 0 | 75.1562 | 0 | 75.1562
IC Recips x 6 | 5050 | 33% | 64.2312 | na | 289.04 | 23.9499 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 96.3152 | 0 | 96.3152
CCCT Dry "G/H", 1x1 | 5050 | 78% | 25.1614 | na | 289.04 | 18.4234 | 2.12 | 10.71% | 0.22712 | 0 | 0 | 45.932 | 0 | 45.932
CCCT Dry "G/H", DF, 1x1 | 5050 | 12% | 83.0898 | na | 289.04 | 26.5107 | 0.15 | 0% | 0 | 0 | 0 | 109.7506 | 0 | 109.7506
CCCT Dry "J/HA.02", 1x1 | 5050 | 78% | 22.6478 | na | 289.04 | 18.2847 | 2.05 | 10.71% | 0.21962 | 0 | 0 | 43.2021 | 0 | 43.2021
CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 12% | 78.9573 | na | 289.04 | 26.6235 | 0.16 | 0% | 0 | 0 | 0 | 105.7408 | 0 | 105.7408
Hunter
SCCT Aero x3 | 5050 | 33% | 56.378 | na | 293.63 | 26.9817 | 8.85 | 12.11% | 1.0717 | 0 | 0 | 93.2813 | 0 | 93.2813
Intercooled SCCT Aero x2 | 5050 | 33% | 43.6727 | na | 293.63 | 26.5207 | 6.14 | 12.11% | 0.74351 | 0 | 0 | 77.0769 | 0 | 77.0769
SCCT Frame "F" x1 | 5050 | 33% | 25.6395 | na | 293.63 | 28.2296 | 6.61 | 13.92% | 0.91999 | 0 | 0 | 61.3991 | 0 | 61.3991
IC Recips x 6 | 5050 | 33% | 51.9941 | na | 293.63 | 24.3302 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 84.4584 | 0 | 84.4584
CCCT Dry "G/H", 1x1 | 5050 | 78% | 21.1788 | na | 293.63 | 18.716 | 2.12 | 10.71% | 0.22712 | 0 | 0 | 42.2419 | 0 | 42.2419
CCCT Dry "G/H", DF, 1x1 | 5050 | 12% | 45.8393 | na | 293.63 | 26.9317 | 0.15 | 0% | 0 | 0 | 0 | 72.921 | 0 | 72.921
CCCT Dry "J/HA.02", 1x1 | 5050 | 78% | 18.6952 | na | 293.63 | 18.575 | 2.05 | 10.71% | 0.21962 | 0 | 0 | 39.5399 | 0 | 39.5399
CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 12% | 41.5484 | na | 293.63 | 27.0463 | 0.16 | 0% | 0 | 0 | 0 | 68.7546 | 0 | 68.7546
Huntington
SCCT Aero x3 | 5050 | 33% | 56.378 | na | 293.63 | 26.9817 | 8.85 | 12.11% | 1.0717 | 0 | 0 | 93.2813 | 0 | 93.2813
Intercooled SCCT Aero x2 | 5050 | 33% | 43.6727 | na | 293.63 | 26.5207 | 6.14 | 12.11% | 0.74351 | 0 | 0 | 77.0769 | 0 | 77.0769
SCCT Frame "F" x1 | 5050 | 33% | 25.6395 | na | 293.63 | 28.2296 | 6.61 | 13.92% | 0.91999 | 0 | 0 | 61.3991 | 0 | 61.3991
IC Recips x 6 | 5050 | 33% | 51.9941 | na | 293.63 | 24.3302 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 84.4584 | 0 | 84.4584
CCCT Dry "G/H", 1x1 | 5050 | 78% | 21.1788 | na | 293.63 | 18.716 | 2.12 | 10.71% | 0.22712 | 0 | 0 | 42.2419 | 0 | 42.2419
CCCT Dry "G/H", DF, 1x1 | 5050 | 12% | 45.8393 | na | 293.63 | 26.9317 | 0.15 | 0% | 0 | 0 | 0 | 72.921 | 0 | 72.921
CCCT Dry "G/H", 2x1 | 5050 | 78% | 16.2096 | na | 293.63 | 18.6895 | 2.01 | 11.33% | 0.22764 | 0 | 0 | 37.1368 | 0 | 37.1368
CCCT Dry "G/H", DF, 2x1 | 5050 | 12% | 39.6916 | na | 293.63 | 26.8407 | 0.16 | 0% | 0 | 0 | 0 | 66.6923 | 0 | 66.6923
CCCT Dry "J/HA.02", 1x1 | 5050 | 78% | 18.6952 | na | 293.63 | 18.575 | 2.05 | 10.71% | 0.21962 | 0 | 0 | 39.5399 | 0 | 39.5399
CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 12% | 41.5484 | na | 293.63 | 27.0463 | 0.16 | 0% | 0 | 0 | 0 | 68.7546 | 0 | 68.7546
|  | Convert to Mills |  |  |  |  | Variable Costs (mills/kWh) |  |  |  |  | Total Costs and Credits (Mills/kWh)
Supply Side Resource Options Mid-Calendar Year 2016 Dollars ($) | Elevation (AFSL) |  |  |  | Levelized Fuel | [7 empty] | Credits
Resource Description |  | Capacity Factor | Total Fixed (Mills/kWh) | Storage Efficiency | ¢/mmBtu | Mills/kWh | O&M | Capitalized Premium | O&M Capitalized | Integration Cost | Environmental | Total Resource Cost | PTC Tax Credits / ITC (Solar Only) | Total Resource Cost - With PTC / ITC Credits
Jim Bridger
SCCT Aero x3 | 6500 | 33% | 59.0601 | na | 288.77 | 26.5524 | 9.6 | 12.11% | 1.1625 | 0 | 0 | 96.375 | 0 | 96.375
Intercooled SCCT Aero x2 | 6500 | 33% | 44.0131 | na | 288.77 | 25.998 | 6.45 | 12.11% | 0.78105 | 0 | 0 | 77.2421 | 0 | 77.2421
SCCT Frame "F" x1 | 6500 | 33% | 24.9573 | na | 288.77 | 27.7364 | 6.96 | 13.92% | 0.9687 | 0 | 0 | 60.6224 | 0 | 60.6224
IC Recips x 6 | 6500 | 33% | 52.456 | na | 288.77 | 24.1903 | 7.75 | 9.183% | 0.71169 | 0 | 0 | 85.108 | 0 | 85.108
CCCT Dry "G/H", 1x1 | 6500 | 78% | 21.8532 | na | 288.77 | 18.4668 | 2.25 | 10.71% | 0.24105 | 0 | 0 | 42.8111 | 0 | 42.8111
CCCT Dry "G/H", DF, 1x1 | 6500 | 12% | 41.5373 | na | 288.77 | 27.5025 | 0.15 | 0% | 0 | 0 | 0 | 69.1898 | 0 | 69.1898
CCCT Dry "J/HA.02", 1x1 | 6500 | 78% | 19.0739 | na | 288.77 | 18.2965 | 2.15 | 10.71% | 0.23033 | 0 | 0 | 39.7507 | 0 | 39.7507
CCCT Dry "J/HA.02", DF, 1x1 | 6500 | 12% | 37.1819 | na | 288.77 | 27.5025 | 0.16 | 0% | 0 | 0 | 0 | 64.8444 | 0 | 64.8444
Naughton
SCCT Aero x3 | 6500 | 33% | 60.7521 | na | 293.63 | 26.9993 | 9.6 | 12.11% | 1.1625 | 0 | 0 | 98.5139 | 0 | 98.5139
Intercooled SCCT Aero x2 | 6500 | 33% | 45.6697 | na | 293.63 | 26.4355 | 6.45 | 12.11% | 0.78105 | 0 | 0 | 79.3363 | 0 | 79.3363
SCCT Frame "F" x1 | 6500 | 33% | 26.7247 | na | 293.63 | 28.2032 | 6.96 | 13.92% | 0.9687 | 0 | 0 | 62.8566 | 0 | 62.8566
IC Recips x 6 | 6500 | 33% | 53.9975 | na | 293.63 | 24.5974 | 7.75 | 9.183% | 0.71169 | 0 | 0 | 87.0566 | 0 | 87.0566
CCCT Dry "J/HA.02", 1x1 | 6500 | 78% | 19.5672 | na | 293.63 | 18.6044 | 2.15 | 10.71% | 0.23033 | 0 | 0 | 40.5519 | 0 | 40.5519
CCCT Dry "J/HA.02", DF, 1x1 | 6500 | 12% | 42.0014 | na | 293.63 | 27.9653 | 0.16 | 0% | 0 | 0 | 0 | 70.1267 | 0 | 70.1267
Wyodak
SCCT Aero x3 | 6500 | 33% | 74.3317 | na | 291.24 | 26.7795 | 9.6 | 12.11% | 1.1625 | 0 | 0 | 111.8737 | 0 | 111.8737
Intercooled SCCT Aero x2 | 6500 | 33% | 58.9658 | na | 291.24 | 26.2203 | 6.45 | 12.11% | 0.78105 | 0 | 0 | 92.4172 | 0 | 92.4172
SCCT Frame "F" x1 | 6500 | 33% | 40.9099 | na | 291.24 | 27.9736 | 6.96 | 13.92% | 0.9687 | 0 | 0 | 76.8122 | 0 | 76.8122
IC Recips x 6 | 6500 | 33% | 66.3691 | na | 291.24 | 24.3972 | 7.75 | 9.183% | 0.71169 | 0 | 0 | 99.2279 | 0 | 99.2279

## Table 6.3
[24 empty] | Capital Cost $/kW |  |  | Fixed Cost | [5 empty] | Convert to Mills |  |  |  |  | Variable Costs (mills/kWh) |  |  |  |  | Total Resource Cost (Mills/kWh) | (mills/kWh) | Total Resource Cost with PTC / ITC (Mills/kWh)
Description |  | Resource Characteristics | [5 empty] | Costs | [5 empty] | Operating Characteristics |  |  |  | Environmental |  |  |  | Supply Side Resource Options Mid-Calendar Year |  | Total Capital Cost | Payment Factor | Annual Payment ($/kW-Yr) | Fixed O&M $/kW-Yr |  |  |  |  | Total Fixed ($/kW-Yr) |  |  |  | Levelized Fuel | [10 empty] | Low |  | Med
Fuel | Resource | Elevation (AFSL) | Net Capacity (MW) | Resource Availability Year | Total Implementation Time (yrs) | Commercial Operation Year | Design Life (yrs) | Base Capital ($/KW) | Var O&M ($/MWh) | Fraction Var O&M Capitalized | Fraction Var O&M Adjusted by Capacity Changes | Fixed O&M ($/KW-yr) | Fraction Fixed O&M Capitalized | Average Full Load Heat Rate (HHV Btu/KWh)/Efficiency | EFOR (%) | POR (%) | Water Consumed (Gal/MWh) | SO2 (lbs/MMBtu) | NOx (lbs/MMBtu) | Hg (lbs/TBTu) | CO2 (lbs/MMBtu) | Resource Description | Elevation (AFSL) |  |  |  | O&M | Capitalized Premium | O&M Capitalized | Gas Transportation | Total |  | Capacity Factor | Total Fixed (Mills/kWh) | Storage Efficiency | ¢/mmBtu | Mills/kWh | O&M | Capitalized Premium | O&M Capitalized | Integration Cost | Environmental |  | PTC Tax Credits / ITC (Solar Only) |  | Capacity Factor | Total Fixed (Mills/kWh) | Capacity Factor | Total Fixed (Mills/kWh) | Table 6.3
Total Resource Cost (Mills/kWh)
[45 empty] | High |  |  |  |  | Capacity Factor CCCT | 40% | 78% | 94%
[50 empty] | Capacity Factor Duct Fire | 10% | 12% | 22%
Natural Gas | CCCT Dry "G/H", 1x1 | 5050 | 337.7907 | 2017 | 4.5036 | 2021.5036 | 40 | 1693.3409 | 2.12 | 0.70112 | 0.93625 | 24.74 | 0.0052116 | 6374 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", 1x1 | 5050 | 1693.3409 | 7.256% | 122.8737 | 24.74 | 0.153% | 0.037864 | 9.7071 | 34.485 | 157.3587 | 94% | 19.1099 | na | 294.97 | 18.8014 | 2.12 | 10.71% | 0.22712 | 0 | 0 | 40.2584 | 0 | 40.2584 | 40% | 44.9083 | 78% | 23.0299 | CCCT Dry "G/H", 1x1 | 66.0568 | 44.1784 | 40.2584
Natural Gas | CCCT Dry "G/H", DF, 1x1 | 5050 | 51.0193 | 2017 | 4.5036 | 2021.5036 | 40 | 442.8693 | 0.15 | 0 | 0.27487 | 5.39 | 0 | 9172 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", DF, 1x1 | 5050 | 442.8693 | 7.256% | 32.1359 | 5.39 | 0% | 0 | 13.9683 | 19.3583 | 51.4941 | 22% | 26.7197 | na | 294.97 | 27.0546 | 0.15 | 0% | 0 | 0 | 0 | 53.9243 | 0 | 53.9243 | 10% | 58.7833 | 12% | 48.9861 | CCCT Dry "G/H", DF, 1x1 | 85.9879 | 76.1907 | 53.9243
Natural Gas | CCCT Dry "G/H", 2x1 | 5050 | 676.5813 | 2017 | 5.5035 | 2022.5035 | 40 | 1257.4204 | 2.01 | 0.73842 | 0.93286 | 16.63 | 0.0077521 | 6365 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", 2x1 | 5050 | 1257.4204 | 7.256% | 91.242 | 16.63 | 0.153% | 0.025452 | 9.6934 | 26.3489 | 117.5909 | 94% | 14.2804 | na | 294.97 | 18.7748 | 2.01 | 11.33% | 0.22764 | 0 | 0 | 35.2929 | 0 | 35.2929 | 40% | 33.5591 | 78% | 17.2098 | CCCT Dry "G/H", 2x1 | 54.5715 | 38.2223 | 35.2929
Natural Gas | CCCT Dry "G/H", DF, 2x1 | 5050 | 102.0032 | 2017 | 5.5035 | 2022.5035 | 40 | 348.0331 | 0.16 | 0 | 0.28015 | 4.44 | 0 | 9141 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", DF, 2x1 | 5050 | 348.0331 | 7.256% | 25.2543 | 4.44 | 0% | 0 | 13.9211 | 18.3611 | 43.6153 | 22% | 22.6315 | na | 294.97 | 26.9632 | 0.16 | 0% | 0 | 0 | 0 | 49.7547 | 0 | 49.7547 | 10% | 49.7892 | 12% | 41.491 | CCCT Dry "G/H", DF, 2x1 | 76.9124 | 68.6142 | 49.7547
Natural Gas | CCCT Dry "J/HA.02", 1x1 | 5050 | 413.5678 | 2017 | 4.5036 | 2021.5036 | 40 | 1476.6324 | 2.05 | 0.70482 | 0.93339 | 21.26 | 0.0049529 | 6326 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", 1x1 | 5050 | 1476.6324 | 7.256% | 107.1487 | 21.26 | 0.153% | 0.032538 | 9.634 | 30.9266 | 138.0753 | 94% | 16.7681 | na | 294.97 | 18.6598 | 2.05 | 10.71% | 0.21962 | 0 | 0 | 37.6975 | 0 | 37.6975 | 40% | 39.405 | 78% | 20.2077 | CCCT Dry "J/HA.02", 1x1 | 60.3345 | 41.1371 | 37.6975
Natural Gas | CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 63.0086 | 2017 | 4.5036 | 2021.5036 | 40 | 378.0723 | 0.16 | 0 | 0.27675 | 4.86 | 0 | 9211 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 378.0723 | 7.256% | 27.434 | 4.86 | 0% | 0 | 14.0277 | 18.8877 | 46.3217 | 22% | 24.0357 | na | 294.97 | 27.1697 | 0.16 | 0% | 0 | 0 | 0 | 51.3654 | 0 | 51.3654 | 10% | 52.8786 | 12% | 44.0655 | CCCT Dry "J/HA.02", DF, 1x1 | 80.2083 | 71.3952 | 51.3654
Natural Gas | CCCT Dry, "J/HA.02" 2X1 | 5050 | 828.3187 | 2017 | 5.5035 | 2022.5035 | 40 | 1099.6822 | 1.95 | 0.73962 | 0.93011 | 14.45 | 0.0072836 | 6317 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry, "J/HA.02" 2X1 | 5050 | 1099.6822 | 7.256% | 79.7961 | 14.45 | 0.153% | 0.022115 | 9.6203 | 24.0924 | 103.8885 | 94% | 12.6164 | na | 294.97 | 18.6333 | 1.95 | 11.33% | 0.22085 | 0 | 0 | 33.4205 | 0 | 33.4205 | 40% | 29.6486 | 78% | 15.2044 | CCCT Dry, "J/HA.02" 2X1 | 50.4527 | 36.0085 | 33.4205
Natural Gas | CCCT Dry "J/HA.02", DF, 2X1 | 5050 | 126.005 | 2017 | 5.5035 | 2022.5035 | 40 | 301.5804 | 0.16 | 0 | 0.2738 | 4.05 | 0 | 9158 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", DF, 2X1 | 5050 | 301.5804 | 7.256% | 21.8835 | 4.05 | 0% | 0 | 13.947 | 17.997 | 39.8805 | 22% | 20.6935 | na | 294.97 | 27.0134 | 0.16 | 0% | 0 | 0 | 0 | 47.8668 | 0 | 47.8668 | 10% | 45.5257 | 12% | 37.9381 | CCCT Dry "J/HA.02", DF, 2X1 | 72.699 | 65.1114 | 47.8668

## Database
|  |  | INPUTS | [21 empty] | Capital Cost $/kW |  |  | Fixed Cost | [5 empty] | Convert to Mills |  |  |  |  | Variable Costs (mills/kWh) |  |  |  |  | Total Costs and Credits (Mills/kWh) | [16 empty] | Convert to Mills
| Description |  | Resource Characteristics | [5 empty] | Costs | [5 empty] | Operating Characteristics |  |  |  | Environmental |  |  |  | Supply Side Resource Options Mid-Calendar Year 2014 Dollars ($) |  |  |  |  | Fixed O&M $/kW-Yr | [8 empty] | Levelized Fuel | [7 empty] | Credits
| Fuel | Resource | Elevation (AFSL) | Net Capacity (MW) | Resource Availability Year | Total Implementation Time (yrs) | Commercial Operation Year | Design Life (yrs) | Base Capital ($/KW) | Var O&M ($/MWh) | Fraction Var O&M Capitalized | Fraction Var O&M Adjusted by Capacity Changes | Fixed O&M ($/KW-yr) | Fraction Fixed O&M Capitalized | Average Full Load Heat Rate (HHV Btu/KWh)/Efficiency | EFOR (%) | POR (%) | Water Consumed (Gal/MWh) | SO2 (lbs/MMBtu) | NOx (lbs/MMBtu) | Hg (lbs/TBTu) | CO2 (lbs/MMBtu) | Resource Description | Elevation (AFSL) | Total Capital Cost | Payment Factor | Annual Payment ($/kW-Yr) | O&M | Capitalized Premium | O&M Capitalized | Gas Transportation | Total | Total Fixed ($/kW-Yr) | Capacity Factor | Total Fixed (Mills/kWh) | Storage Efficiency | ¢/mmBtu | Mills/kWh | O&M | Capitalized Premium | O&M Capitalized | Integration Cost | Environmental | Total Resource Cost | PTC Tax Credits / ITC (Solar Only) | Total Resource Cost - With PTC / ITC Credits | ID | Location | Resource | Location Code | Location and Resource | Turbine | Non Renewable/Nuclear | Tax | PTC | Wind/Solar Integration | % PTC | Storage | Resource Cost | Index | Capacity Factor
1 | Natural Gas | SCCT Aero x3, ISO | 0 | 141.9097 | 2017 | 4.0845 | 2021.0845 | 30 | 1420.5567 | 7.54 | 0.90653 | 0.97815 | 27.14 | 0.10353 | 9204 | 2.6 | 3.85 | 58 | 0.0006 | 0.009 | 0.255 | 117 | SCCT Aero x3, ISO | 0 | 1420.5567 | 7.871% | 111.8134 | 27.14 | 1.331% | 0.36115 | 32.9684 | 60.4695 | 172.2829 | 33% | 59.597 | na | 294.97 | 27.149 | 7.54 | 12.11% | 0.91304 | 0 | 0 | 95.1991 | 0 | 95.1991 | 1 | Pacific Northwest | SC_Aero | I_PNC_ | I_PNC_SC_Aero | Single Cycle Combustion Turbine (SCCT) Aero | Fuel |  |  | Null |  |  |  |  | 33%
2 | Natural Gas | Intercooled SCCT Aero x2, ISO | 0 | 220.6745 | 2017 | 4.0845 | 2021.0845 | 30 | 1036.2994 | 5.05 | 0.9051 | 0.96637 | 18.78 | 0.089283 | 8981 | 2.9 | 3.85 | 80 | 0.0006 | 0.009 | 0.255 | 117 | Intercooled SCCT Aero x2, ISO | 0 | 1036.2994 | 7.871% | 81.5681 | 18.78 | 1.198% | 0.22491 | 32.1696 | 51.1745 | 132.7427 | 33% | 45.919 | na | 294.97 | 26.4913 | 5.05 | 12.11% | 0.61152 | 0 | 0 | 78.0718 | 0 | 78.0718 | 2 | Pacific Northwest | SC_ICAero | I_PNC_ | I_PNC_SC_ICAero | Intercooled SCCT Aero | Fuel |  |  | Null |  |  |  |  | 33%
3 | Natural Gas | SCCT Frame "F" x1, ISO | 0 | 240.2941 | 2017 | 4.0845 | 2021.0845 | 35 | 583.7288 | 5.5 | 0.96516 | 0.97059 | 13.28 | 0.020272 | 9604 | 2.7 | 3.85 | 20 | 0.0006 | 0.009 | 0.255 | 117 | SCCT Frame "F" x1, ISO | 0 | 583.7288 | 7.373% | 43.0362 | 13.28 | 0.287% | 0.03811 | 34.4012 | 47.7193 | 90.7555 | 33% | 31.3946 | na | 294.97 | 28.3289 | 5.5 | 13.92% | 0.7655 | 0 | 0 | 65.989 | 0 | 65.989 | 3 | Pacific Northwest | SC_Frame | I_PNC_ | I_PNC_SC_Frame | Single Cycle Combustion Turbine (SCCT) Frame | Fuel |  |  | Null |  |  |  |  | 33%
4 | Natural Gas | IC Recips x 6, ISO | 0 | 110.5535 | 2017 | 4.0845 | 2021.0845 | 35 | 1572.4256 | 7.45 | 0.63857 | 0.87527 | 29.82 | 0.014142 | 8279 | 2.5 | 5 | 5 | 0.0006 | 0.0288 | 0.255 | 117 | IC Recips x 6, ISO | 0 | 1572.4256 | 7.871% | 123.7671 | 29.82 | 0.1435% | 0.042787 | 29.6551 | 59.5179 | 183.285 | 33% | 63.4029 | na | 294.97 | 24.4206 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 95.9576 | 0 | 95.9576 | 4 | Pacific Northwest | SC_ICE | I_PNC_ | I_PNC_SC_ICE | Internal Combustion Engines | Fuel |  |  | Null |  |  |  |  | 33%
5 | Natural Gas | CCCT Dry "G/H", 1x1, ISO | 0 | 407.1465 | 2017 | 4.5036 | 2021.5036 | 40 | 1404.8872 | 1.76 | 0.70112 | 0.93625 | 20.52 | 0.0052116 | 6363 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", 1x1, ISO | 0 | 1404.8872 | 7.256% | 101.9427 | 20.52 | 0.153% | 0.031405 | 22.792 | 43.3434 | 145.2861 | 78% | 21.263 | na | 294.97 | 18.7689 | 1.76 | 10.71% | 0.18855 | 0 | 0 | 41.9805 | 0 | 41.9805 | 5 | Pacific Northwest | CC_GH_1x1 | I_PNC_ | I_PNC_CC_GH_1x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
6 | Natural Gas | CCCT Dry "G/H", DF, 1x1, ISO | 0 | 51.0003 | 2017 | 4.5036 | 2021.5036 | 40 | 443.0343 | 0.15 | 0 | 0.27487 | 5.39 | 0 | 8865 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", DF, 1x1, ISO | 0 | 443.0343 | 7.256% | 32.1478 | 5.39 | 0% | 0 | 31.7541 | 37.1441 | 69.292 | 12% | 65.917 | na | 294.97 | 26.1491 | 0.15 | 0% | 0 | 0 | 0 | 92.2161 | 0 | 92.2161 | 6 | Pacific Northwest | CC_GH_1x1_DF | I_PNC_ | I_PNC_CC_GH_1x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
7 | Natural Gas | CCCT Dry "G/H", 2x1, ISO | 0 | 815.6922 | 2017 | 5.5035 | 2022.5035 | 40 | 1042.9757 | 1.67 | 0.73842 | 0.93286 | 13.79 | 0.0077521 | 6352 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", 2x1, ISO | 0 | 1042.9757 | 7.256% | 75.6813 | 13.79 | 0.153% | 0.021105 | 22.7526 | 36.5637 | 112.2451 | 78% | 16.4274 | na | 294.97 | 18.7365 | 1.67 | 11.33% | 0.18913 | 0 | 0 | 37.023 | 0 | 37.023 | 7 | Pacific Northwest | CC_GH_2x1 | I_PNC_ | I_PNC_CC_GH_2x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
8 | Natural Gas | CCCT Dry "G/H", DF, 2x1, ISO | 0 | 101.9939 | 2017 | 5.5035 | 2022.5035 | 40 | 348.0646 | 0.16 | 0 | 0.28015 | 4.44 | 0 | 8812 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", DF, 2x1, ISO | 0 | 348.0646 | 7.256% | 25.2566 | 4.44 | 0% | 0 | 31.5643 | 36.0043 | 61.2608 | 12% | 58.2771 | na | 294.97 | 25.9928 | 0.16 | 0% | 0 | 0 | 0 | 84.4298 | 0 | 84.4298 | 8 | Pacific Northwest | CC_GH_2x1_DF | I_PNC_ | I_PNC_CC_GH_2x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
9 | Natural Gas | CCCT Dry "J/HA.02", 1x1, ISO | 0 | 498.03 | 2017 | 4.5036 | 2021.5036 | 40 | 1226.2066 | 1.7 | 0.70482 | 0.93339 | 17.66 | 0.0049529 | 6317 | 2.5 | 3.8 | 0 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", 1x1, ISO | 0 | 1226.2066 | 7.256% | 88.9771 | 17.66 | 0.153% | 0.027028 | 22.6273 | 40.3143 | 129.2914 | 78% | 18.9222 | na | 294.97 | 18.6333 | 1.7 | 10.71% | 0.18213 | 0 | 0 | 39.4375 | 0 | 39.4375 | 13 | Pacific Northwest | CC_J_1x1 | I_PNC_ | I_PNC_CC_J_1x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
10 | Natural Gas | CCCT Dry "J/HA.02", DF, 1x1, ISO | 0 | 62.9999 | 2017 | 4.5036 | 2021.5036 | 40 | 378.1246 | 0.16 | 0 | 0.27675 | 4.86 | 0 | 8878 | 0.8 | 3.8 | 0 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", DF, 1x1, ISO | 0 | 378.1246 | 7.256% | 27.4378 | 4.86 | 0% | 0 | 31.8007 | 36.6607 | 64.0985 | 12% | 60.9765 | na | 294.97 | 26.1874 | 0.16 | 0% | 0 | 0 | 0 | 87.3239 | 0 | 87.3239 | 14 | Pacific Northwest | CC_J_1x1_DF | I_PNC_ | I_PNC_CC_J_1x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
11 | Natural Gas | CCCT Dry, "J/HA.02" 2X1, ISO | 0 | 997.6192 | 2017 | 5.5035 | 2022.5035 | 40 | 913.0611 | 1.62 | 0.73962 | 0.93011 | 12 | 0.0072836 | 6308 | 2.5 | 3.8 | 0 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry, "J/HA.02" 2X1, ISO | 0 | 913.0611 | 7.256% | 66.2543 | 12 | 0.153% | 0.018366 | 22.595 | 34.6134 | 100.8677 | 78% | 14.7623 | na | 294.97 | 18.6067 | 1.62 | 11.33% | 0.18347 | 0 | 0 | 35.1725 | 0 | 35.1725 | 15 | Pacific Northwest | CC_J_2x1 | I_PNC_ | I_PNC_CC_J_2x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
12 | Natural Gas | CCCT Dry "J/HA.02", DF, 2X1, ISO | 0 | 125.9959 | 2017 | 5.5035 | 2022.5035 | 40 | 301.6021 | 0.16 | 0 | 0.2738 | 4.05 | 0 | 8830 | 0.8 | 3.8 | 0 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", DF, 2X1, ISO | 0 | 301.6021 | 7.256% | 21.8851 | 4.05 | 0% | 0 | 31.6287 | 35.6787 | 57.5639 | 12% | 54.7601 | na | 294.97 | 26.0459 | 0.16 | 0% | 0 | 0 | 0 | 80.966 | 0 | 80.966 | 16 | Pacific Northwest | CC_J_2x1_DF | I_PNC_ | I_PNC_CC_J_2x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
13 | Natural Gas | SCCT Aero x3 | 1500 | 137.7394 | 2017 | 4.0845 | 2021.0845 | 30 | 1463.5665 | 7.76 | 0.90653 | 0.97815 | 27.96 | 0.10353 | 9169 | 2.6 | 3.85 | 58 | 0.0006 | 0.009 | 0.255 | 117 | SCCT Aero x3 | 1500 | 1463.5665 | 7.871% | 115.1987 | 27.96 | 1.331% | 0.37206 | 32.843 | 61.1751 | 176.3738 | 33% | 61.0121 | na | 294.97 | 27.0458 | 7.76 | 12.11% | 0.93968 | 0 | 0 | 96.7576 | 0 | 96.7576 | 17 | Walla Walla | SC_Aero | I_WW_ | I_WW_SC_Aero | Single Cycle Combustion Turbine (SCCT) Aero | Fuel |  |  | Null |  |  |  |  | 33%
14 | Natural Gas | Intercooled SCCT Aero x2 | 1500 | 208.4491 | 2017 | 4.0845 | 2021.0845 | 30 | 1097.0774 | 5.35 | 0.9051 | 0.96637 | 19.88 | 0.089283 | 9000 | 2.9 | 3.85 | 80 | 0.0006 | 0.009 | 0.255 | 117 | Intercooled SCCT Aero x2 | 1500 | 1097.0774 | 7.871% | 86.352 | 19.88 | 1.198% | 0.23809 | 32.2377 | 52.3558 | 138.7078 | 33% | 47.9825 | na | 294.97 | 26.5473 | 5.35 | 12.11% | 0.64785 | 0 | 0 | 80.5276 | 0 | 80.5276 | 18 | Walla Walla | SC_ICAero | I_WW_ | I_WW_SC_ICAero | Intercooled SCCT Aero | Fuel |  |  | Null |  |  |  |  | 33%
15 | Natural Gas | SCCT Frame "F" x1 | 1500 | 227.6546 | 2017 | 4.0845 | 2021.0845 | 35 | 616.1377 | 5.81 | 0.96516 | 0.97059 | 14.02 | 0.020272 | 9604 | 2.7 | 3.85 | 20 | 0.0006 | 0.009 | 0.255 | 117 | SCCT Frame "F" x1 | 1500 | 616.1377 | 7.373% | 45.4256 | 14.02 | 0.287% | 0.040233 | 34.4012 | 48.4614 | 93.887 | 33% | 32.4779 | na | 294.97 | 28.3289 | 5.81 | 13.92% | 0.80864 | 0 | 0 | 67.4254 | 0 | 67.4254 | 19 | Walla Walla | SC_Frame | I_WW_ | I_WW_SC_Frame | Single Cycle Combustion Turbine (SCCT) Frame | Fuel |  |  | Null |  |  |  |  | 33%
16 | Natural Gas | IC Recips x 6 | 1500 | 110.5535 | 2017 | 4.0845 | 2021.0845 | 35 | 1572.4256 | 7.45 | 0.63857 | 0.87527 | 29.82 | 0.014142 | 8279 | 2.5 | 5 | 5 | 0.0006 | 0.0288 | 0.255 | 117 | IC Recips x 6 | 1500 | 1572.4256 | 7.871% | 123.7671 | 29.82 | 0.1435% | 0.042787 | 29.6551 | 59.5179 | 183.285 | 33% | 63.4029 | na | 294.97 | 24.4206 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 95.9576 | 0 | 95.9576 | 20 | Walla Walla | SC_ICE | I_WW_ | I_WW_SC_ICE | Internal Combustion Engines | Fuel |  |  | Null |  |  |  |  | 33%
17 | Natural Gas | CCCT Dry "G/H", 1x1 | 1500 | 385.3535 | 2017 | 4.5036 | 2021.5036 | 40 | 1484.3381 | 1.86 | 0.70112 | 0.93625 | 21.68 | 0.0052116 | 6362 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", 1x1 | 1500 | 1484.3381 | 7.256% | 107.7078 | 21.68 | 0.153% | 0.03318 | 22.7885 | 44.5016 | 152.2095 | 78% | 22.2763 | na | 294.97 | 18.766 | 1.86 | 10.71% | 0.19927 | 0 | 0 | 43.1016 | 0 | 43.1016 | 21 | Walla Walla | CC_GH_1x1 | I_WW_ | I_WW_CC_GH_1x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
18 | Natural Gas | CCCT Dry "G/H", DF, 1x1 | 1500 | 51.0037 | 2017 | 4.5036 | 2021.5036 | 40 | 443.0044 | 0.15 | 0 | 0.27487 | 5.39 | 0 | 9012 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", DF, 1x1 | 1500 | 443.0044 | 7.256% | 32.1457 | 5.39 | 0% | 0 | 32.2807 | 37.6707 | 69.8163 | 12% | 66.4158 | na | 294.97 | 26.5827 | 0.15 | 0% | 0 | 0 | 0 | 93.1485 | 0 | 93.1485 | 22 | Walla Walla | CC_GH_1x1_DF | I_WW_ | I_WW_CC_GH_1x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
19 | Natural Gas | CCCT Dry "G/H", 2x1 | 1500 | 771.8273 | 2017 | 5.5035 | 2022.5035 | 40 | 1102.2506 | 1.77 | 0.73842 | 0.93286 | 14.57 | 0.0077521 | 6353 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", 2x1 | 1500 | 1102.2506 | 7.256% | 79.9825 | 14.57 | 0.153% | 0.022299 | 22.7562 | 37.3485 | 117.331 | 78% | 17.1717 | na | 294.97 | 18.7394 | 1.77 | 11.33% | 0.20046 | 0 | 0 | 37.8816 | 0 | 37.8816 | 23 | Walla Walla | CC_GH_2x1 | I_WW_ | I_WW_CC_GH_2x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
20 | Natural Gas | CCCT Dry "G/H", DF, 2x1 | 1500 | 101.9937 | 2017 | 5.5035 | 2022.5035 | 40 | 348.0655 | 0.16 | 0 | 0.28015 | 4.44 | 0 | 8969 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", DF, 2x1 | 1500 | 348.0655 | 7.256% | 25.2566 | 4.44 | 0% | 0 | 32.1266 | 36.5666 | 61.8233 | 12% | 58.8121 | na | 294.97 | 26.4559 | 0.16 | 0% | 0 | 0 | 0 | 85.4279 | 0 | 85.4279 | 24 | Walla Walla | CC_GH_2x1_DF | I_WW_ | I_WW_CC_GH_2x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
21 | Natural Gas | CCCT Dry "J/HA.02", 1x1 | 1500 | 470.9438 | 2017 | 4.5036 | 2021.5036 | 40 | 1296.7314 | 1.8 | 0.70482 | 0.93339 | 18.67 | 0.0049529 | 6317 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", 1x1 | 1500 | 1296.7314 | 7.256% | 94.0946 | 18.67 | 0.153% | 0.028574 | 22.6273 | 41.3258 | 135.4204 | 78% | 19.8192 | na | 294.97 | 18.6333 | 1.8 | 10.71% | 0.19284 | 0 | 0 | 40.4453 | 0 | 40.4453 | 29 | Walla Walla | CC_J_1x1 | I_WW_ | I_WW_CC_J_1x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
22 | Natural Gas | CCCT Dry "J/HA.02", DF, 1x1 | 1500 | 63.004 | 2017 | 4.5036 | 2021.5036 | 40 | 378.1 | 0.16 | 0 | 0.27675 | 4.86 | 0 | 9035 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", DF, 1x1 | 1500 | 378.1 | 7.256% | 27.436 | 4.86 | 0% | 0 | 32.363 | 37.223 | 64.6591 | 12% | 61.5098 | na | 294.97 | 26.6505 | 0.16 | 0% | 0 | 0 | 0 | 88.3203 | 0 | 88.3203 | 30 | Walla Walla | CC_J_1x1_DF | I_WW_ | I_WW_CC_J_1x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
23 | Natural Gas | CCCT Dry, "J/HA.02" 2X1 | 1500 | 943.7244 | 2017 | 5.5035 | 2022.5035 | 40 | 965.2047 | 1.71 | 0.73962 | 0.93011 | 12.69 | 0.0072836 | 6304 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry, "J/HA.02" 2X1 | 1500 | 965.2047 | 7.256% | 70.038 | 12.69 | 0.153% | 0.019422 | 22.5807 | 35.2901 | 105.3282 | 78% | 15.4151 | na | 294.97 | 18.5949 | 1.71 | 11.33% | 0.19366 | 0 | 0 | 35.9137 | 0 | 35.9137 | 31 | Walla Walla | CC_J_2x1 | I_WW_ | I_WW_CC_J_2x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
24 | Natural Gas | CCCT Dry "J/HA.02", DF, 2X1 | 1500 | 126.0048 | 2017 | 5.5035 | 2022.5035 | 40 | 301.5809 | 0.16 | 0 | 0.2738 | 4.05 | 0 | 8906 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", DF, 2X1 | 1500 | 301.5809 | 7.256% | 21.8836 | 4.05 | 0% | 0 | 31.901 | 35.951 | 57.8345 | 12% | 55.0176 | na | 294.97 | 26.27 | 0.16 | 0% | 0 | 0 | 0 | 81.4477 | 0 | 81.4477 | 32 | Walla Walla | CC_J_2x1_DF | I_WW_ | I_WW_CC_J_2x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
25 | Natural Gas | SCCT Aero x3 | 3000 | 130.2074 | 2017 | 4.0845 | 2021.0845 | 30 | 1548.2276 | 8.21 | 0.90653 | 0.97815 | 29.58 | 0.10353 | 9183 | 2.6 | 3.85 | 58 | 0.0006 | 0.009 | 0.255 | 117 | SCCT Aero x3 | 3000 | 1548.2276 | 7.871% | 121.8625 | 29.58 | 1.331% | 0.39362 | 16.8477 | 46.8213 | 168.6838 | 33% | 58.3519 | na | 293.35 | 26.9383 | 8.21 | 12.11% | 0.99417 | 0 | 0 | 94.4944 | 0 | 94.4944 | 33 | Southern Oregon - California | SC_Aero | I_SO_ | I_SO_SC_Aero | Single Cycle Combustion Turbine (SCCT) Aero | Fuel |  |  | Null |  |  |  |  | 33%
26 | Natural Gas | Intercooled SCCT Aero x2 | 3000 | 196.4388 | 2017 | 4.0845 | 2021.0845 | 30 | 1164.1529 | 5.67 | 0.9051 | 0.96637 | 21.1 | 0.089283 | 9016 | 2.9 | 3.85 | 80 | 0.0006 | 0.009 | 0.255 | 117 | Intercooled SCCT Aero x2 | 3000 | 1164.1529 | 7.871% | 91.6316 | 21.1 | 1.198% | 0.2527 | 16.5413 | 37.894 | 129.5256 | 33% | 44.8061 | na | 293.35 | 26.4484 | 5.67 | 12.11% | 0.6866 | 0 | 0 | 77.6112 | 0 | 77.6112 | 34 | Southern Oregon - California | SC_ICAero | I_SO_ | I_SO_SC_ICAero | Intercooled SCCT Aero | Fuel |  |  | Null |  |  |  |  | 33%
27 | Natural Gas | SCCT Frame "F" x1 | 3000 | 215.6017 | 2017 | 4.0845 | 2021.0845 | 35 | 650.5821 | 6.13 | 0.96516 | 0.97059 | 14.81 | 0.020272 | 9611 | 2.7 | 3.85 | 20 | 0.0006 | 0.009 | 0.255 | 117 | SCCT Frame "F" x1 | 3000 | 650.5821 | 7.373% | 47.965 | 14.81 | 0.287% | 0.0425 | 17.6329 | 32.4854 | 80.4504 | 33% | 27.8298 | na | 293.35 | 28.1939 | 6.13 | 13.92% | 0.85318 | 0 | 0 | 63.0069 | 0 | 63.0069 | 35 | Southern Oregon - California | SC_Frame | I_SO_ | I_SO_SC_Frame | Single Cycle Combustion Turbine (SCCT) Frame | Fuel |  |  | Null |  |  |  |  | 33%
28 | Natural Gas | IC Recips x 6 | 3000 | 110.5535 | 2017 | 4.0845 | 2021.0845 | 35 | 1572.4256 | 7.45 | 0.63857 | 0.87527 | 29.82 | 0.014142 | 8279 | 2.5 | 5 | 5 | 0.0006 | 0.0288 | 0.255 | 117 | IC Recips x 6 | 3000 | 1572.4256 | 7.871% | 123.7671 | 29.82 | 0.1435% | 0.042787 | 15.1891 | 45.0519 | 168.8191 | 33% | 58.3987 | na | 293.35 | 24.2864 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 90.8193 | 0 | 90.8193 | 36 | Southern Oregon - California | SC_ICE | I_SO_ | I_SO_SC_ICE | Internal Combustion Engines | Fuel |  |  | Null |  |  |  |  | 33%
29 | Natural Gas | CCCT Dry "G/H", 1x1 | 3000 | 364.5319 | 2017 | 4.5036 | 2021.5036 | 40 | 1569.1214 | 1.97 | 0.70112 | 0.93625 | 22.92 | 0.0052116 | 6366 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", 1x1 | 3000 | 1569.1214 | 7.256% | 113.86 | 22.92 | 0.153% | 0.035078 | 11.6794 | 34.6345 | 148.4945 | 78% | 21.7326 | na | 293.35 | 18.6747 | 1.97 | 10.71% | 0.21105 | 0 | 0 | 42.5883 | 0 | 42.5883 | 37 | Southern Oregon - California | CC_GH_1x1 | I_SO_ | I_SO_CC_GH_1x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
30 | Natural Gas | CCCT Dry "G/H", DF, 1x1 | 3000 | 51.0013 | 2017 | 4.5036 | 2021.5036 | 40 | 443.0253 | 0.15 | 0 | 0.27487 | 5.39 | 0 | 9055 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", DF, 1x1 | 3000 | 443.0253 | 7.256% | 32.1472 | 5.39 | 0% | 0 | 16.6128 | 22.0028 | 54.15 | 12% | 51.5126 | na | 293.35 | 26.5628 | 0.15 | 0% | 0 | 0 | 0 | 78.2254 | 0 | 78.2254 | 38 | Southern Oregon - California | CC_GH_1x1_DF | I_SO_ | I_SO_CC_GH_1x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
31 | Natural Gas | CCCT Dry "G/H", 2x1 | 3000 | 730.7083 | 2017 | 5.5035 | 2022.5035 | 40 | 1164.2775 | 1.86 | 0.73842 | 0.93286 | 15.39 | 0.0077521 | 6352 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", 2x1 | 3000 | 1164.2775 | 7.256% | 84.4833 | 15.39 | 0.153% | 0.023554 | 11.6538 | 27.0673 | 111.5506 | 78% | 16.3258 | na | 293.35 | 18.6336 | 1.86 | 11.33% | 0.21065 | 0 | 0 | 37.03 | 0 | 37.03 | 39 | Southern Oregon - California | CC_GH_2x1 | I_SO_ | I_SO_CC_GH_2x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
32 | Natural Gas | CCCT Dry "G/H", DF, 2x1 | 3000 | 101.9466 | 2017 | 5.5035 | 2022.5035 | 40 | 348.2264 | 0.16 | 0 | 0.28015 | 4.44 | 0 | 9012 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", DF, 2x1 | 3000 | 348.2264 | 7.256% | 25.2683 | 4.44 | 0% | 0 | 16.534 | 20.974 | 46.2423 | 12% | 43.99 | na | 293.35 | 26.4367 | 0.16 | 0% | 0 | 0 | 0 | 70.5867 | 0 | 70.5867 | 40 | Southern Oregon - California | CC_GH_2x1_DF | I_SO_ | I_SO_CC_GH_2x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
33 | Natural Gas | CCCT Dry "J/HA.02", 1x1 | 3000 | 445.5988 | 2017 | 4.5036 | 2021.5036 | 40 | 1370.4877 | 1.9 | 0.70482 | 0.93339 | 19.73 | 0.0049529 | 6321 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", 1x1 | 3000 | 1370.4877 | 7.256% | 99.4465 | 19.73 | 0.153% | 0.030196 | 11.5969 | 31.3571 | 130.8036 | 78% | 19.1435 | na | 293.35 | 18.5427 | 1.9 | 10.71% | 0.20355 | 0 | 0 | 39.7897 | 0 | 39.7897 | 45 | Southern Oregon - California | CC_J_1x1 | I_SO_ | I_SO_CC_J_1x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
34 | Natural Gas | CCCT Dry "J/HA.02", DF, 1x1 | 3000 | 62.9978 | 2017 | 4.5036 | 2021.5036 | 40 | 378.1374 | 0.16 | 0 | 0.27675 | 4.86 | 0 | 9087 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", DF, 1x1 | 3000 | 378.1374 | 7.256% | 27.4387 | 4.86 | 0% | 0 | 16.6716 | 21.5316 | 48.9703 | 12% | 46.5851 | na | 293.35 | 26.6567 | 0.16 | 0% | 0 | 0 | 0 | 73.4018 | 0 | 73.4018 | 46 | Southern Oregon - California | CC_J_1x1_DF | I_SO_ | I_SO_CC_J_1x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
35 | Natural Gas | CCCT Dry, "J/HA.02" 2X1 | 3000 | 892.9227 | 2017 | 5.5035 | 2022.5035 | 40 | 1020.1188 | 1.81 | 0.73962 | 0.93011 | 13.41 | 0.0072836 | 6308 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry, "J/HA.02" 2X1 | 3000 | 1020.1188 | 7.256% | 74.0228 | 13.41 | 0.153% | 0.020524 | 11.573 | 25.0036 | 99.0263 | 78% | 14.4928 | na | 293.35 | 18.5045 | 1.81 | 11.33% | 0.20499 | 0 | 0 | 35.0123 | 0 | 35.0123 | 47 | Southern Oregon - California | CC_J_2x1 | I_SO_ | I_SO_CC_J_2x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
36 | Natural Gas | CCCT Dry "J/HA.02", DF, 2X1 | 3000 | 126.0006 | 2017 | 5.5035 | 2022.5035 | 40 | 301.591 | 0.16 | 0 | 0.2738 | 4.05 | 0 | 9039 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", DF, 2X1 | 3000 | 301.591 | 7.256% | 21.8843 | 4.05 | 0% | 0 | 16.5835 | 20.6335 | 42.5178 | 12% | 40.4469 | na | 293.35 | 26.5159 | 0.16 | 0% | 0 | 0 | 0 | 67.1228 | 0 | 67.1228 | 48 | Southern Oregon - California | CC_J_2x1_DF | I_SO_ | I_SO_CC_J_2x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
37 | Natural Gas | SCCT Aero x3 | 5050 | 120.8637 | 2017 | 4.0845 | 2021.0845 | 30 | 1667.9175 | 8.85 | 0.90653 | 0.97815 | 31.86 | 0.10353 | 9189 | 2.6 | 3.85 | 58 | 0.0006 | 0.009 | 0.255 | 117 | SCCT Aero x3 | 5050 | 1667.9175 | 7.871% | 131.2834 | 31.86 | 1.331% | 0.42396 | 13.9942 | 46.2781 | 177.5615 | 33% | 61.423 | na | 294.97 | 27.1048 | 8.85 | 12.11% | 1.0717 | 0 | 0 | 98.4494 | 0 | 98.4494 | 49 | Utah South | SC_Aero | I_US_ | I_US_SC_Aero | Single Cycle Combustion Turbine (SCCT) Aero | Fuel |  |  | Null |  |  |  |  | 33%
38 | Natural Gas | Intercooled SCCT Aero x2 | 5050 | 181.6303 | 2017 | 4.0845 | 2021.0845 | 30 | 1259.0673 | 6.14 | 0.9051 | 0.96637 | 22.82 | 0.089283 | 9032 | 2.9 | 3.85 | 80 | 0.0006 | 0.009 | 0.255 | 117 | Intercooled SCCT Aero x2 | 5050 | 1259.0673 | 7.871% | 99.1024 | 22.82 | 1.198% | 0.2733 | 13.7551 | 36.8484 | 135.9508 | 33% | 47.0288 | na | 294.97 | 26.6417 | 6.14 | 12.11% | 0.74351 | 0 | 0 | 80.554 | 0 | 80.554 | 50 | Utah South | SC_ICAero | I_US_ | I_US_SC_ICAero | Intercooled SCCT Aero | Fuel |  |  | Null |  |  |  |  | 33%
39 | Natural Gas | SCCT Frame "F" x1 | 5050 | 199.9241 | 2017 | 4.0845 | 2021.0845 | 35 | 701.5991 | 6.61 | 0.96516 | 0.97059 | 15.97 | 0.020272 | 9614 | 2.7 | 3.85 | 20 | 0.0006 | 0.009 | 0.255 | 117 | SCCT Frame "F" x1 | 5050 | 701.5991 | 7.373% | 51.7263 | 15.97 | 0.287% | 0.045829 | 14.6414 | 30.6572 | 82.3836 | 33% | 28.4985 | na | 294.97 | 28.3584 | 6.61 | 13.92% | 0.91999 | 0 | 0 | 64.3869 | 0 | 64.3869 | 51 | Utah South | SC_Frame | I_US_ | I_US_SC_Frame | Single Cycle Combustion Turbine (SCCT) Frame | Fuel |  |  | Null |  |  |  |  | 33%
40 | Natural Gas | IC Recips x 6 | 5050 | 110.5535 | 2017 | 4.0845 | 2021.0845 | 35 | 1572.4256 | 7.45 | 0.63857 | 0.87527 | 29.82 | 0.014142 | 8286 | 2.5 | 5 | 5 | 0.0006 | 0.0288 | 0.255 | 117 | IC Recips x 6 | 5050 | 1572.4256 | 7.871% | 123.7671 | 29.82 | 0.1435% | 0.042787 | 12.619 | 42.4818 | 166.2489 | 33% | 57.5096 | na | 294.97 | 24.4412 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 90.085 | 0 | 90.085 | 52 | Utah South | SC_ICE | I_US_ | I_US_SC_ICE | Internal Combustion Engines | Fuel |  |  | Null |  |  |  |  | 33%
41 | Natural Gas | CCCT Dry "G/H", 1x1 | 5050 | 337.7907 | 2017 | 4.5036 | 2021.5036 | 40 | 1693.3409 | 2.12 | 0.70112 | 0.93625 | 24.74 | 0.0052116 | 6374 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", 1x1 | 5050 | 1693.3409 | 7.256% | 122.8737 | 24.74 | 0.153% | 0.037864 | 9.7071 | 34.485 | 157.3587 | 78% | 23.0299 | na | 294.97 | 18.8014 | 2.12 | 10.71% | 0.22712 | 0 | 0 | 44.1784 | 0 | 44.1784 | 53 | Utah South | CC_GH_1x1 | I_US_ | I_US_CC_GH_1x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
42 | Natural Gas | CCCT Dry "G/H", DF, 1x1 | 5050 | 51.0193 | 2017 | 4.5036 | 2021.5036 | 40 | 442.8693 | 0.15 | 0 | 0.27487 | 5.39 | 0 | 9172 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", DF, 1x1 | 5050 | 442.8693 | 7.256% | 32.1359 | 5.39 | 0% | 0 | 13.9683 | 19.3583 | 51.4941 | 12% | 48.9861 | na | 294.97 | 27.0546 | 0.15 | 0% | 0 | 0 | 0 | 76.1907 | 0 | 76.1907 | 54 | Utah South | CC_GH_1x1_DF | I_US_ | I_US_CC_GH_1x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
43 | Natural Gas | CCCT Dry "G/H", 2x1 | 5050 | 676.5813 | 2017 | 5.5035 | 2022.5035 | 40 | 1257.4204 | 2.01 | 0.73842 | 0.93286 | 16.63 | 0.0077521 | 6365 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", 2x1 | 5050 | 1257.4204 | 7.256% | 91.242 | 16.63 | 0.153% | 0.025452 | 9.6934 | 26.3489 | 117.5909 | 78% | 17.2098 | na | 294.97 | 18.7748 | 2.01 | 11.33% | 0.22764 | 0 | 0 | 38.2223 | 0 | 38.2223 | 55 | Utah South | CC_GH_2x1 | I_US_ | I_US_CC_GH_2x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
44 | Natural Gas | CCCT Dry "G/H", DF, 2x1 | 5050 | 102.0032 | 2017 | 5.5035 | 2022.5035 | 40 | 348.0331 | 0.16 | 0 | 0.28015 | 4.44 | 0 | 9141 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", DF, 2x1 | 5050 | 348.0331 | 7.256% | 25.2543 | 4.44 | 0% | 0 | 13.9211 | 18.3611 | 43.6153 | 12% | 41.491 | na | 294.97 | 26.9632 | 0.16 | 0% | 0 | 0 | 0 | 68.6142 | 0 | 68.6142 | 56 | Utah South | CC_GH_2x1_DF | I_US_ | I_US_CC_GH_2x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
45 | Natural Gas | CCCT Dry "J/HA.02", 1x1 | 5050 | 413.5678 | 2017 | 4.5036 | 2021.5036 | 40 | 1476.6324 | 2.05 | 0.70482 | 0.93339 | 21.26 | 0.0049529 | 6326 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", 1x1 | 5050 | 1476.6324 | 7.256% | 107.1487 | 21.26 | 0.153% | 0.032538 | 9.634 | 30.9266 | 138.0753 | 78% | 20.2077 | na | 294.97 | 18.6598 | 2.05 | 10.71% | 0.21962 | 0 | 0 | 41.1371 | 0 | 41.1371 | 61 | Utah South | CC_J_1x1 | I_US_ | I_US_CC_J_1x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
46 | Natural Gas | CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 63.0086 | 2017 | 4.5036 | 2021.5036 | 40 | 378.0723 | 0.16 | 0 | 0.27675 | 4.86 | 0 | 9211 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 378.0723 | 7.256% | 27.434 | 4.86 | 0% | 0 | 14.0277 | 18.8877 | 46.3217 | 12% | 44.0655 | na | 294.97 | 27.1697 | 0.16 | 0% | 0 | 0 | 0 | 71.3952 | 0 | 71.3952 | 62 | Utah South | CC_J_1x1_DF | I_US_ | I_US_CC_J_1x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
47 | Natural Gas | CCCT Dry, "J/HA.02" 2X1 | 5050 | 828.3187 | 2017 | 5.5035 | 2022.5035 | 40 | 1099.6822 | 1.95 | 0.73962 | 0.93011 | 14.45 | 0.0072836 | 6317 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry, "J/HA.02" 2X1 | 5050 | 1099.6822 | 7.256% | 79.7961 | 14.45 | 0.153% | 0.022115 | 9.6203 | 24.0924 | 103.8885 | 78% | 15.2044 | na | 294.97 | 18.6333 | 1.95 | 11.33% | 0.22085 | 0 | 0 | 36.0085 | 0 | 36.0085 | 63 | Utah South | CC_J_2x1 | I_US_ | I_US_CC_J_2x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
48 | Natural Gas | CCCT Dry "J/HA.02", DF, 2X1 | 5050 | 126.005 | 2017 | 5.5035 | 2022.5035 | 40 | 301.5804 | 0.16 | 0 | 0.2738 | 4.05 | 0 | 9158 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", DF, 2X1 | 5050 | 301.5804 | 7.256% | 21.8835 | 4.05 | 0% | 0 | 13.947 | 17.997 | 39.8805 | 12% | 37.9381 | na | 294.97 | 27.0134 | 0.16 | 0% | 0 | 0 | 0 | 65.1114 | 0 | 65.1114 | 64 | Utah South | CC_J_2x1_DF | I_US_ | I_US_CC_J_2x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
49 | Natural Gas | SCCT Aero x3 | 6500 | 111.4125 | 2017 | 4.0845 | 2021.0845 | 30 | 1809.4081 | 9.6 | 0.90653 | 0.97815 | 34.56 | 0.10353 | 9195 | 2.6 | 3.85 | 58 | 0.0006 | 0.009 | 0.255 | 117 | SCCT Aero x3 | 6500 | 1809.4081 | 7.871% | 142.4203 | 34.56 | 1.331% | 0.45989 | 9.1121 | 44.132 | 186.5522 | 33% | 64.5331 | na | 289.01 | 26.5745 | 9.6 | 12.11% | 1.1625 | 0 | 0 | 101.87 | 0 | 101.87 | 66 | WY-SW | SC_Aero | I_WSW_ | I_WSW_SC_Aero | Single Cycle Combustion Turbine (SCCT) Aero | Fuel |  |  | Null |  |  |  |  | 33%
50 | Natural Gas | Intercooled SCCT Aero x2 | 6500 | 172.6999 | 2017 | 4.0845 | 2021.0845 | 30 | 1324.1743 | 6.45 | 0.9051 | 0.96637 | 24 | 0.089283 | 9003 | 2.9 | 3.85 | 80 | 0.0006 | 0.009 | 0.255 | 117 | Intercooled SCCT Aero x2 | 6500 | 1324.1743 | 7.871% | 104.227 | 24 | 1.198% | 0.28743 | 8.9218 | 33.2092 | 137.4363 | 33% | 47.5426 | na | 289.01 | 26.0196 | 6.45 | 12.11% | 0.78105 | 0 | 0 | 80.7933 | 0 | 80.7933 | 67 | WY-SW | SC_ICAero | I_WSW_ | I_WSW_SC_ICAero | Intercooled SCCT Aero | Fuel |  |  | Null |  |  |  |  | 33%
51 | Natural Gas | SCCT Frame "F" x1 | 6500 | 189.8403 | 2017 | 4.0845 | 2021.0845 | 35 | 738.8661 | 6.96 | 0.96516 | 0.97059 | 16.81 | 0.020272 | 9605 | 2.7 | 3.85 | 20 | 0.0006 | 0.009 | 0.255 | 117 | SCCT Frame "F" x1 | 6500 | 738.8661 | 7.373% | 54.4739 | 16.81 | 0.287% | 0.04824 | 9.5184 | 26.3766 | 80.8505 | 33% | 27.9682 | na | 289.01 | 27.7594 | 6.96 | 13.92% | 0.9687 | 0 | 0 | 63.6563 | 0 | 63.6563 | 68 | WY-SW | SC_Frame | I_WSW_ | I_WSW_SC_Frame | Single Cycle Combustion Turbine (SCCT) Frame | Fuel |  |  | Null |  |  |  |  | 33%
52 | Natural Gas | IC Recips x 6 | 6500 | 106.1894 | 2017 | 4.0845 | 2021.0845 | 35 | 1637.0477 | 7.75 | 0.63857 | 0.87527 | 31.04 | 0.014142 | 8377 | 2.5 | 5 | 5 | 0.0006 | 0.0288 | 0.255 | 117 | IC Recips x 6 | 6500 | 1637.0477 | 7.871% | 128.8536 | 31.04 | 0.1435% | 0.044538 | 8.3015 | 39.386 | 168.2396 | 33% | 58.1983 | na | 289.01 | 24.2104 | 7.75 | 9.183% | 0.71169 | 0 | 0 | 90.8703 | 0 | 90.8703 | 69 | WY-SW | SC_ICE | I_WSW_ | I_WSW_SC_ICE | Internal Combustion Engines | Fuel |  |  | Null |  |  |  |  | 33%
53 | Natural Gas | CCCT Dry "G/H", 1x1 | 6500 | 318.9379 | 2017 | 4.5036 | 2021.5036 | 40 | 1793.4362 | 2.25 | 0.70112 | 0.93625 | 26.2 | 0.0052116 | 6395 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", 1x1 | 6500 | 1793.4362 | 7.256% | 130.1369 | 26.2 | 0.153% | 0.040098 | 6.3373 | 32.5774 | 162.7143 | 78% | 23.8137 | na | 289.01 | 18.4822 | 2.25 | 10.71% | 0.24105 | 0 | 0 | 44.7869 | 0 | 44.7869 | 70 | WY-SW | CC_GH_1x1 | I_WSW_ | I_WSW_CC_GH_1x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
54 | Natural Gas | CCCT Dry "G/H", DF, 1x1 | 6500 | 51.0052 | 2017 | 4.5036 | 2021.5036 | 40 | 442.9914 | 0.15 | 0 | 0.27487 | 5.39 | 0 | 9524 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", DF, 1x1 | 6500 | 442.9914 | 7.256% | 32.1447 | 5.39 | 0% | 0 | 9.4381 | 14.8281 | 46.9728 | 12% | 44.685 | na | 289.01 | 27.5253 | 0.15 | 0% | 0 | 0 | 0 | 72.3603 | 0 | 72.3603 | 71 | WY-SW | CC_GH_1x1_DF | I_WSW_ | I_WSW_CC_GH_1x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
55 | Natural Gas | CCCT Dry "G/H", 2x1 | 6500 | 638.8732 | 2017 | 5.5035 | 2022.5035 | 40 | 1331.6368 | 2.13 | 0.73842 | 0.93286 | 17.61 | 0.0077521 | 6385 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", 2x1 | 6500 | 1331.6368 | 7.256% | 96.6274 | 17.61 | 0.153% | 0.026951 | 6.3274 | 23.9644 | 120.5918 | 78% | 17.649 | na | 289.01 | 18.4533 | 2.13 | 11.33% | 0.24123 | 0 | 0 | 38.4735 | 0 | 38.4735 | 72 | WY-SW | CC_GH_2x1 | I_WSW_ | I_WSW_CC_GH_2x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
56 | Natural Gas | CCCT Dry "G/H", DF, 2x1 | 6500 | 102.0197 | 2017 | 5.5035 | 2022.5035 | 40 | 347.9768 | 0.16 | 0 | 0.28015 | 4.44 | 0 | 9461 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "G/H", DF, 2x1 | 6500 | 347.9768 | 7.256% | 25.2502 | 4.44 | 0% | 0 | 9.3757 | 13.8157 | 39.0659 | 12% | 37.1631 | na | 289.01 | 27.3432 | 0.16 | 0% | 0 | 0 | 0 | 64.6664 | 0 | 64.6664 | 73 | WY-SW | CC_GH_2x1_DF | I_WSW_ | I_WSW_CC_GH_2x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
57 | Natural Gas | CCCT Dry "J/HA.02", 1x1 | 6500 | 393.7563 | 2017 | 4.5036 | 2021.5036 | 40 | 1550.928 | 2.15 | 0.70482 | 0.93339 | 22.33 | 0.0049529 | 6336 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", 1x1 | 6500 | 1550.928 | 7.256% | 112.5398 | 22.33 | 0.153% | 0.034175 | 6.2789 | 28.643 | 141.1828 | 78% | 20.6625 | na | 289.01 | 18.3117 | 2.15 | 10.71% | 0.23033 | 0 | 0 | 41.3545 | 0 | 41.3545 | 78 | WY-SW | CC_J_1x1 | I_WSW_ | I_WSW_CC_J_1x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
58 | Natural Gas | CCCT Dry "J/HA.02", DF, 1x1 | 6500 | 63.0098 | 2017 | 4.5036 | 2021.5036 | 40 | 378.0653 | 0.16 | 0 | 0.27675 | 4.86 | 0 | 9524 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", DF, 1x1 | 6500 | 378.0653 | 7.256% | 27.4335 | 4.86 | 0% | 0 | 9.4381 | 14.2981 | 41.7316 | 12% | 39.699 | na | 289.01 | 27.5253 | 0.16 | 0% | 0 | 0 | 0 | 67.3843 | 0 | 67.3843 | 79 | WY-SW | CC_J_1x1_DF | I_WSW_ | I_WSW_CC_J_1x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
59 | Natural Gas | CCCT Dry, "J/HA.02" 2X1 | 6500 | 788.6039 | 2017 | 5.5035 | 2022.5035 | 40 | 1155.0631 | 2.05 | 0.73962 | 0.93011 | 15.18 | 0.0072836 | 6327 | 2.5 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry, "J/HA.02" 2X1 | 6500 | 1155.0631 | 7.256% | 83.8147 | 15.18 | 0.153% | 0.023232 | 6.2699 | 21.4732 | 105.2879 | 78% | 15.4092 | na | 289.01 | 18.2857 | 2.05 | 11.33% | 0.23217 | 0 | 0 | 35.977 | 0 | 35.977 | 80 | WY-SW | CC_J_2x1 | I_WSW_ | I_WSW_CC_J_2x1 | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 78%
60 | Natural Gas | CCCT Dry "J/HA.02", DF, 2X1 | 6500 | 125.936 | 2017 | 5.5035 | 2022.5035 | 40 | 301.7457 | 0.16 | 0 | 0.2738 | 4.06 | 0 | 9469 | 0.8 | 3.8 | 11 | 0.0006 | 0.0072 | 0.255 | 117 | CCCT Dry "J/HA.02", DF, 2X1 | 6500 | 301.7457 | 7.256% | 21.8955 | 4.06 | 0% | 0 | 9.3836 | 13.4436 | 35.3391 | 12% | 33.6179 | na | 289.01 | 27.3664 | 0.16 | 0% | 0 | 0 | 0 | 61.1443 | 0 | 61.1443 | 81 | WY-SW | CC_J_2x1_DF | I_WSW_ | I_WSW_CC_J_2x1_DF | Combined Cycle Combustion Turbine (CCCT) | Fuel |  |  | Null |  |  |  |  | 12%
82
61 | Coal | SCPC with CCS | 4500 | 526 | 2027 | 7 | 2034 | 40 | 6077.664 | 6.71 | 0 | 0 | 69.2162 | 0.38 | 13087 | 5 | 5 | 1004.2373 | 0.0085 | 0.07 | 0.022222 | 20.5352 | SCPC with CCS | 4500 | 6077.664 | 7.157% | 434.9807 | 69.2162 |  | 0 | 0 | 69.2162 | 504.1969 | 90.25% | 63.7748 | na |  |  | 6.71 |  |  |  |  | NC | 0 | NC | 83 |  |  |  |  | Coal (Pulverized) with CCS Weighted | [8 empty] | 90.25%
| Coal | Not Used |  |  |  |  | 0 | [15 empty] | Not Used | [23 empty] | 84
62 | Coal | IGCC with CCS | 4500 | 466 | 2027 | 7 | 2034 | 40 | 5884.4667 | 11.28 | 0.79 | 0 | 55.7752 | 0 | 10823 | 8 | 7 | 394.0678 | 0.0085 | 0.05 | 0.33333 | 20.5352 | IGCC with CCS | 4500 | 5884.4667 | 6.853% | 403.2856 | 55.7752 |  | 0 | 0 | 55.7752 | 459.0608 | 85.56% | 61.2485 | na |  |  | 11.28 |  |  |  |  | NC | 0 | NC | 85 |  |  |  |  | IGCC (Power Block, Gasifier, CCS weighted) | [8 empty] | 85.56%
| Coal | Not Used |  |  |  |  | 0 | [15 empty] | Not Used | [23 empty] | 86
63 | Coal | PC CCS retrofit @ 500 MW | 4500 | -139 | 2027 | 4 | 2031 | 20 | 1334.3443 | 6.2017 | 0 | 0 | 74.5171 | 0.38 | 14372 | 5 | 5 | 1004.2373 | 0.005 | 0.07 | 1.2 | 20.5352 | PC CCS retrofit @ 500 MW | 4500 | 1334.3443 | 7.157% | 95.4995 | 74.5171 |  | 0 | 0 | 74.5171 | 170.0166 | 90.25% | 21.505 | na |  |  | 6.2017 |  |  |  |  | NC | 0 | NC | 87 | [13 empty] | 90.25%
64 | Coal | SCPC with CCS | 6500 | 692 | 2027 | 7 | 2034 | 40 | 6882.6526 | 7.26 | 0 | 0 | 64.2924 | 0.38 | 13242 | 5 | 5 | 1004.2373 | 0.0085 | 0.07 | 0.022222 | 20.5352 | SCPC with CCS | 6500 | 6882.6526 | 7.157% | 492.594 | 64.2924 |  | 0 | 0 | 64.2924 | 556.8864 | 90.25% | 70.4393 | na |  |  | 7.26 |  |  |  |  | NC | 0 | NC | 88 |  |  |  |  | Coal (Pulverized) with CCS Weighted | [8 empty] | 90.25%
| Coal | Not Used | 0 | 0 |  |  | 0 | [15 empty] | Not Used | [23 empty] | 89
65 | Coal | IGCC with CCS | 6500 | 456 | 2027 | 7 | 2034 | 40 | 6663.0057 | 13.52 | 0.79 | 0 | 60.7619 | 0 | 11047 | 8 | 7 | 394.0678 | 0.0085 | 0.05 | 0.33333 | 20.5352 | IGCC with CCS | 6500 | 6663.0057 | 6.853% | 456.6419 | 60.7619 |  | 0 | 0 | 60.7619 | 517.4038 | 85.56% | 69.0327 | na |  |  | 13.52 |  |  |  |  | NC | 0 | NC | 90 |  |  |  |  | IGCC (Power Block, Gasifier, CCS weighted) | [8 empty] | 85.56%
| Coal | Not Used | 0 | 0 |  |  | 0 | [15 empty] | Not Used | [23 empty] | 91
66 | Coal | PC CCS retrofit @ 500 MW | 6500 | -139 | 2027 | 4 | 2031 | 20 | 1511.0786 | 6.71 | 0 | 0 | 69.2162 | 0.38 | 14372 | 5 | 5 | 1004.2373 | 0.005 | 0.07 | 1.2 | 20.5352 | PC CCS retrofit @ 500 MW | 6500 | 1511.0786 | 7.135% | 107.821 | 69.2162 |  | 0 | 0 | 69.2162 | 177.0372 | 90.25% | 22.3931 | na |  |  | 6.71 |  |  |  |  | NC | 0 | NC | 92 | [13 empty] | 90.25%
93
67 | Geothermal | Blundell Dual Flash 90% CF | 4500 | 35 | 2017 | 4.0845 | 2021.0845 | 40 | 6130.8225 | 1.12 | 0 | 0 | 100.51 | 0.058786 | n/a | 5 | 5 | 10 | n/a | n/a | n/a | n/a | Blundell Dual Flash 90% CF | 4500 | 6130.8225 | 6.311% | 386.9416 | 100.51 | 0.9183% | 0.92296 | 0 | 101.433 | 488.3745 | 90.25% | 61.7734 | na | 0 | 0 | 1.12 | 0% | 0 | 0 | 0 | 62.8934 | -19.9842 | 42.9092 | 94 | Utah South | GEO_B35 | I_US_ | I_US_GEO_B35 | Geothermal |  | Tax | PTC | Null | Unit |  |  |  | 90.25%
68 | Geothermal | Greenfield Binary 90% CF | 4500 | 43 | 2017 | 5.5035 | 2022.5035 | 40 | 6793.2297 | 1.1246 | 0 | 0 | 100.5063 | 0.058786 | n/a | 5 | 5 | 270 | n/a | n/a | n/a | n/a | Greenfield Binary 90% CF | 4500 | 6793.2297 | 6.311% | 428.7488 | 100.5063 | 0.9183% | 0.92293 | 0 | 101.4292 | 530.1781 | 90.25% | 67.0611 | na | 0 | 0 | 1.1246 | 0% | 0 | 0 | 0 | 68.1857 | -19.9842 | 48.2015 | 95 | Utah South | GEO_B35 | I_US_ | I_US_GEO_B35 | Geothermal | [8 empty] | 90.25%
69 | Geothermal | Generic Geothermal PPA 90% CF | 4500 | 30 | 2017 | 4.0845 | 2021.0845 | 20 | 0 | 77.34 | 0 | 0 | 0 | 0 | n/a | 5 | 5 | 270 | n/a | n/a | n/a | n/a | Generic Geothermal PPA 90% CF | 4500 | 0 | 6.311% | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 90.25% | 0 | na | 0 | 0 | 77.34 | 0% | 0 | 0 | 0 | 77.34 | 0 | 77.34 | 96 | Utah South | GEO_PPA | I_US_ | I_US_GEO_PPA | Geothermal |  |  |  | Null |  |  |  |  | 90.25%
97
70 | Wind | 2.0 MW turbine 38% CF WA,2021 | 1500 | 100 | 2017 | 5.0022 | 2022.0022 | 30 | 1799.7506 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 38% CF WA,2021 | 1500 | 1799.7506 | 7.067% | 127.1971 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 164.7627 | 35% | 53.7387 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 54.3117 | -19.9842 | 34.3274 | 98 | Yakima | WD | I_YK_ | I_YK_WD | Wind |  | Tax | PTC | Wind Integration | Wind100 |  | 54.3117 | 134 | 35%
71 | Wind | 2.0 MW turbine 38% CF OR, 2021 | 1500 | 100 | 2017 | 5.0022 | 2022.0022 | 30 | 1773.9008 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 38% CF OR, 2021 | 1500 | 1773.9008 | 7.067% | 125.3702 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 162.9358 | 35% | 53.1428 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 53.7158 | -19.9842 | 33.7316 | 99 | Southern Oregon - California | WD_T | I_SO_ | I_SO_WD_T | Wind |  | Tax | PTC | Wind Integration | Wind100 |  | 53.7158 | 135 | 35%
72 | Wind | 2.0 MW turbine 38% CF ID, 2021 | 4500 | 100 | 2017 | 5.0022 | 2022.0022 | 30 | 1811.0329 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 38% CF ID, 2021 | 4500 | 1811.0329 | 7.067% | 127.9945 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 165.5601 | 35% | 53.9987 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 54.5717 | -19.9842 | 34.5875 | 100 | Goshen | WD | I_GO_ | I_GO_WD | Wind |  | Tax | PTC | Wind Integration | Wind100 |  | 54.5717 | 136 | 35%
73 | Wind | 2.0 MW turbine 31% CF UT, 2021 | 4500 | 100 | 2017 | 5.0022 | 2022.0022 | 30 | 1735.3716 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 31% CF UT, 2021 | 4500 | 1735.3716 | 7.067% | 122.6471 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 160.2127 | 31% | 58.9972 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 59.5702 | -19.9842 | 39.586 | 101 | Utah South | WD | I_US_ | I_US_WD | Wind |  | Tax | PTC | Wind Integration | Wind100 |  | 59.5702 | 137 | 31%
74 | Wind | 3.3 MW turbine 43% CF WY, 2021 | 6500 | 100 | 2017 | 5.0022 | 2022.0022 | 30 | 1737.2477 | 0.65 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | 3.3 MW turbine 43% CF WY, 2021 | 6500 | 1737.2477 | 7.067% | 122.7797 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 160.3453 | 43% | 42.568 | na | 0 | 0 | 0.65 | 0% | 0 | 0.573 | 0 | 43.791 | -19.9842 | 23.8068 | 102 | Wyoming-AE | WD | I_WAE_ | I_WAE_WD | Wind |  | Tax | PTC | Wind Integration | Wind100 |  | 43.791 | 138 | 43%
75 | Wind | 2.0 MW turbine 38% CF WA,2024 | 1500 | 100 | 2017 | 5.0022 | 2023 | 30 | 1799.7506 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 38% CF WA,2024 | 1500 | 1799.7506 | 7.067% | 127.1971 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 164.7627 | 38% | 49.4961 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 50.0691 | -7.9937 | 42.0754 | 103 | Yakima | WD | I_YK_ | I_YK_WD | Wind |  | Tax | PTC | Wind Integration | Wind40 |  | 50.0691 | 139 | 38%
76 | Wind | 2.0 MW turbine 38% CF OR, 2024 | 1500 | 100 | 2017 | 5.0022 | 2023 | 30 | 1773.9008 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 38% CF OR, 2024 | 1500 | 1773.9008 | 7.067% | 125.3702 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 162.9358 | 38% | 48.9473 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 49.5203 | -7.9937 | 41.5266 | 104 | Southern Oregon - California | WD_T | I_SO_ | I_SO_WD_T | Wind |  | Tax | PTC | Wind Integration | Wind40 |  | 49.5203 | 140 | 38%
77 | Wind | 2.0 MW turbine 38% CF ID, 2024 | 4500 | 100 | 2017 | 5.0022 | 2023 | 30 | 1811.0329 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 38% CF ID, 2024 | 4500 | 1811.0329 | 7.067% | 127.9945 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 165.5601 | 38% | 49.7357 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 50.3087 | -7.9937 | 42.315 | 105 | Goshen | WD | I_GO_ | I_GO_WD | Wind |  | Tax | PTC | Wind Integration | Wind40 |  | 50.3087 | 141 | 38%
78 | Wind | 2.0 MW turbine 31% CF UT, 2024 | 4500 | 100 | 2017 | 5.0022 | 2023 | 30 | 1735.3716 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 31% CF UT, 2024 | 4500 | 1735.3716 | 7.067% | 122.6471 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 160.2127 | 31% | 58.9972 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 59.5702 | -7.9937 | 51.5765 | 106 | Utah South | WD | I_US_ | I_US_WD | Wind |  | Tax | PTC | Wind Integration | Wind40 |  | 59.5702 | 142 | 31%
79 | Wind | 3.3 MW turbine 43% CF WY, 2024 | 6500 | 100 | 2017 | 5.0022 | 2023 | 30 | 1737.2477 | 0.65 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | 3.3 MW turbine 43% CF WY, 2024 | 6500 | 1737.2477 | 7.067% | 122.7797 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 160.3453 | 43% | 42.568 | na | 0 | 0 | 0.65 | 0% | 0 | 0.573 | 0 | 43.791 | -7.9937 | 35.7974 | 107 | Wyoming-AE | WD | I_WAE_ | I_WAE_WD | Wind |  | Tax | PTC | Wind Integration | Wind40 |  | 43.791 | 143 | 43%
108
80 | Solar | PV Poly-Si Fixed Tilt 26.8% AC CF (1.35 MWdc/Mwac) UT, 2019 | 4500 | 50 | 2017 | 1.9998 | 2018.9998 | 25 | 1723.7488 | 0 | 0 | 0 | 18.45 | 0.12467 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Fixed Tilt 26.8% AC CF (1.35 MWdc/Mwac) UT, 2019 | 4500 | 1723.7488 | 7.716% | 132.9989 | 18.45 | 1.461% | 0.26953 | 0 | 18.7195 | 151.7184 | 26.8% | 64.6248 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 65.2278 | -8.84 | 56.3879 | 109 | Utah South | PV50FT | I_US_ | I_US_PV50FT | Solar - Rooftop Photovoltaic |  | Tax | PTC | Solar Integration |  |  | 56.3879 | 144 | 26.8%
81 | Solar | PV Poly-Si Single Tracking 31.1% AC CF (1.25 MWdc/Mwac) UT, 2019 | 4500 | 50 | 2017 | 1.9998 | 2018.9998 | 25 | 1822.4072 | 0 | 0 | 0 | 19.41 | 0.11851 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Single Tracking 31.1% AC CF (1.25 MWdc/Mwac) UT, 2019 | 4500 | 1822.4072 | 7.716% | 140.6111 | 19.41 | 1.461% | 0.28356 | 0 | 19.6936 | 160.3046 | 31.1% | 58.8412 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 59.4442 | -8.0537 | 51.3905 | 110 | Utah South | PV50ST | I_US_ | I_US_PV50ST | Solar - Rooftop Photovoltaic |  | Tax | PTC | Solar Integration |  |  | 51.3905 | 145 | 31.1%
82 | Solar | PV Poly-Si Fixed Tilt 24.9% AC CF (1.35 MWdc/Mwac) OR, 2019 | 4800 | 50 | 2017 | 2 | 2019 | 25 | 1761.8948 | 0 | 0 | 0 | 18.47 | 0.12451 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Fixed Tilt 24.9% AC CF (1.35 MWdc/Mwac) OR, 2019 | 4800 | 1761.8948 | 7.716% | 135.9421 | 18.47 | 1.461% | 0.26983 | 0 | 18.7398 | 154.682 | 24.9% | 70.9147 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 71.5177 | -9.7251 | 61.7926 | 111 | Southern Oregon - California | PV50FT | I_SO_ | I_SO_PV50FT | Solar - Rooftop Photovoltaic |  | Tax | PTC | Solar Integration |  |  | 61.7926 | 146 | 24.9%
83 | Solar | PV Poly-Si Single Tracking 28.8% AC CF (1.25 MWdc/Mwac) OR, 2019 | 4800 | 50 | 2017 | 2 | 2019 | 25 | 1856.7386 | 0 | 0 | 0 | 19.44 | 0.11833 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Single Tracking 28.8% AC CF (1.25 MWdc/Mwac) OR, 2019 | 4800 | 1856.7386 | 7.716% | 143.26 | 19.44 | 1.461% | 0.284 | 0 | 19.724 | 162.984 | 28.8% | 64.6023 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 65.2053 | -8.8608 | 56.3446 | 112 | Southern Oregon - California | PV50ST | I_SO_ | I_SO_PV50ST | Solar - Rooftop Photovoltaic |  | Tax | PTC | Solar Integration |  |  | 56.3446 | 147 | 28.8%
84 | Solar | PV Poly-Si Fixed Tilt 26.8% AC CF (1.35 MWdc/Mwac) UT, 2023 | 4500 | 50 | 2017 | 1.9998 | 2023 | 25 | 1723.7488 | 0 | 0 | 0 | 18.45 | 0.12467 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Fixed Tilt 26.8% AC CF (1.35 MWdc/Mwac) UT, 2023 | 4500 | 1723.7488 | 7.716% | 132.9989 | 18.45 | 1.461% | 0.26953 | 0 | 18.7195 | 151.7184 | 26.8% | 64.6248 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 65.2278 | -5.9119 | 59.316 | 113 | Utah South | PV50FT | I_US_ | I_US_PV50FT | Solar - Rooftop Photovoltaic |  | Tax | PTC | Solar Integration |  |  | 59.316 | 148 | 26.8%
85 | Solar | PV Poly-Si Single Tracking 31.1% AC CF (1.25 MWdc/Mwac) UT, 2023 | 4500 | 50 | 2017 | 1.9998 | 2023 | 25 | 1822.4072 | 0 | 0 | 0 | 19.41 | 0.11851 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Single Tracking 31.1% AC CF (1.25 MWdc/Mwac) UT, 2023 | 4500 | 1822.4072 | 7.716% | 140.6111 | 19.41 | 1.461% | 0.28356 | 0 | 19.6936 | 160.3046 | 31.1% | 58.8412 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 59.4442 | -5.386 | 54.0582 | 114 | Utah South | PV50ST | I_US_ | I_US_PV50ST | Solar - Rooftop Photovoltaic |  | Tax | PTC | Solar Integration |  |  | 54.0582 | 149 | 31.1%
86 | Solar | PV Poly-Si Fixed Tilt 24.9% AC CF (1.35 MWdc/Mwac) OR, 2023 | 4800 | 50 | 2017 | 2 | 2023 | 25 | 1761.8948 | 0 | 0 | 0 | 18.47 | 0.12451 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Fixed Tilt 24.9% AC CF (1.35 MWdc/Mwac) OR, 2023 | 4800 | 1761.8948 | 7.716% | 135.9421 | 18.47 | 1.461% | 0.26983 | 0 | 18.7398 | 154.682 | 24.9% | 70.9147 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 71.5177 | -6.5038 | 65.0139 | 115 | Southern Oregon - California | PV50FT | I_SO_ | I_SO_PV50FT | Solar - Rooftop Photovoltaic |  | Tax | PTC | Solar Integration |  |  | 65.0139 | 150 | 24.9%
87 | Solar | PV Poly-Si Single Tracking 28.8% AC CF (1.25 MWdc/Mwac) OR, 2023 | 4800 | 50 | 2017 | 2 | 2023 | 25 | 1856.7386 | 0 | 0 | 0 | 19.44 | 0.11833 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Single Tracking 28.8% AC CF (1.25 MWdc/Mwac) OR, 2023 | 4800 | 1856.7386 | 7.716% | 143.26 | 19.44 | 1.461% | 0.284 | 0 | 19.724 | 162.984 | 28.8% | 64.6023 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 65.2053 | -5.9258 | 59.2796 | 116 | Southern Oregon - California | PV50ST | I_SO_ | I_SO_PV50ST | Solar - Rooftop Photovoltaic |  | Tax | PTC | Solar Integration |  |  | 59.2796 | 151 | 28.8%
| Solar | Not Used | 0 | 0 |  |  | 0 | [15 empty] | Not Used |  | 0 | [21 empty] | 117
88 | Solar | CSP Trough w Natural Gas | 4500 | 100 | 2017 | 5 | 2022 | 30 | 6447.5397 | 0 | 0 | 0 | 68.4642 | 0.39303 | 11750 | Included with CF |  | 725 | n/a | n/a | n/a | n/a | CSP Trough w Natural Gas | 4500 | 6447.5397 | 7.067% | 455.679 | 68.4642 | 0% | 0 | 17.8995 | 86.3638 | 542.0427 | 33% | 187.5061 | na | 293.96 | 7.3669 | 0 | 0% | 0 | 0.603 | 0 | 195.476 | -8.5882 | 186.8879 | 118 |  |  |  |  | Biomass | [5 empty] | 2506.0909 |  |  | 33%
89 | Solar | CSP Tower 24% CF | 4500 | 100 | 2017 | 5 | 2022 | 30 | 6141.4654 | 0 | 0 | 0 | 68.4642 | 0.39303 | n/a | Included with CF |  | 725 | n/a | n/a | n/a | n/a | CSP Tower 24% CF | 4500 | 6141.4654 | 7.067% | 434.0472 | 68.4642 | 0% | 0 | 0 | 68.4642 | 502.5114 | 24% | 239.018 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 239.621 | -11.2481 | 228.3728 | 119 |  |  |  |  | Biomass | [8 empty] | 24%
90 | Solar | CSP Tower Molten Salt 30% CF | 4500 | 100 | 2017 | 5 | 2022 | 30 | 7367.0328 | 0 | 0 | 0 | 68.4642 | 0.39303 | n/a | Included with CF |  | 750 | n/a | n/a | n/a | n/a | CSP Tower Molten Salt 30% CF | 4500 | 7367.0328 | 7.067% | 520.664 | 68.4642 | 0% | 0 | 0 | 68.4642 | 589.1282 | 30% | 224.1736 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 224.7766 | -10.7942 | 213.9824 | 120 |  |  |  |  | Biomass | [8 empty] | 30%
121
91 | Biomass | Forestry Byproduct | 1500 | 5 | 2017 | 5.0022 | 2022.0022 | 30 | 4383.3025 | 0.99 | 0 | 0 | 42.04 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.4 | 205 | Forestry Byproduct | 1500 | 4383.3025 | 7.067% | 309.7893 | 42.04 |  | 0 | 0 | 42.04 | 351.8293 | 91% | 44.1353 | na |  |  | 0.99 |  |  |  |  | NC | 0 | NC | 122 |  |  |  |  | Biomass | [8 empty] | 91%
123
92 | Storage | Pumped Storage 1 (3,800 MWh) | 4457 | 393.3 | 2017 | 5.0022 | 2022.0022 | 50 | 3468.3873 | 0 | 0 | 0 | 21.1 | 0 | 77% | 3 | 5.8 | 0 | 0 | 0 | 0 | 0 | Pumped Storage 1 (3,800 MWh) | 4457 | 3468.3873 | 6.517% | 226.047 | 21.1 | 0% | 0 | 0 | 21.1 | 247.147 | 40.26% | 70.0814 | 77% | 293.35 | 24.0318 | 0 | 0% | 0 | 0 | 0 | 94.1132 | 0 | 94.1132 | 124 | Southern Oregon - California | PUMP | I_SO_ | I_SO_PUMP | Pumped Storage | Fuel |  |  | Null | Null | 6308 |  |  | 40.26%
93 | Storage | Pumped Storage 2 (12,000 MWh) | 580 | 1200 | 2017 | 5.0022 | 2022.0022 | 50 | 3600.6916 | 0 | 0 | 0 | 15.58 | 0 | 77% | 3 | 5.8 | 0 | 0 | 0 | 0 | 0 | Pumped Storage 2 (12,000 MWh) | 580 | 3600.6916 | 6.517% | 234.6697 | 15.58 | 0% | 0 | 0 | 15.58 | 250.2497 | 41.67% | 68.5616 | 77% | 289.01 | 23.6763 | 0 | 0% | 0 | 0 | 0 | 92.2379 | 0 | 92.2379 | 125 | WY-SW | PUMP | I_WSW_ | I_WSW_PUMP | Pumped Storage | Fuel |  |  | Null | Null | 6308 |  |  | 41.67%
94 | Storage | Pumped Storage 3 (7,000 MWh) | 6359 | 700 | 2017 | 0 | 2017 | 50 | 2860.7143 | 0 | 0 | 0 | 16.86 | 0 | 77% | 3 | 5.8 | 0 | 0 | 0 | 0 | 0 | Pumped Storage 3 (7,000 MWh) | 6359 | 2860.7143 | 6.517% | 186.4428 | 16.86 | 0% | 0 | 0 | 16.86 | 203.3028 | 41.67% | 55.6994 | 77% | 294.97 | 24.1646 | 0 | 0% | 0 | 0 | 0 | 79.8639 | 0 | 79.8639 | 126 | Walla Walla | PUMP | I_WW_ | I_WW_PUMP | Pumped Storage | Fuel |  |  | Null | Null | 6308 |  |  | 41.67%
| Storage | Not Used |  | 0 | 2017 | 0 | 2017 | 0 | [14 empty] | Not Used | [23 empty] | 127
| Storage | Not Used |  | 0 | 2017 | 0 | 2017 | 0 | [14 empty] | Not Used | [23 empty] | 128
95 | Storage | CAES (15,360 MWh) | 4640 | 320 | 2018 | 3.0024 | 2021.0024 | 30 | 2138.2486 | 0.77 | 0.41 | 0 | 18.9 | 0 | 4227 | 3 | 1.5 | 0 | 0.001 | 0.009 | 0 | 117 | CAES (15,360 MWh) | 4640 | 2138.2486 | 7.871% | 168.3036 | 18.9 | 0% | 0 | 0 | 18.9 | 187.2036 | 30% | 71.2343 | 50% | 294.97 | 24.9368 | 0.77 | 5.456% | 0.04201 | 0 | 0 | 96.983 | 0 | 96.983 | 129 | Utah South | CAES | I_US_ | I_US_CAES | Compressed Air Energy Storage (CAES) | Fuel |  |  | Null | Null | 4227 |  |  | 30% | Ian Andrews 30 to 35%
130
96 | Nuclear | Advanced Fission | 5000 | 2234 | 2020 | 4.7502 | 2024.7502 | 40 | 6524.1573 | 11.37 | 0 | 0 | 98.35 | 0.38 | 10710 | 7.7 | 7.3 | 96.0028 | 0 | 0 | 0 | 0 | Advanced Fission | 5000 | 6524.1573 | 7.018% | 457.8859 | 98.35 | 5.816% | 5.7198 | 0 | 104.0698 | 561.9557 | 85.56% | 74.975 | na | 0 | 0 | 11.37 | 0% | 0 | 0 | 0 | 86.345 | 0 | 86.345 | 131 | WY-SW | NUC_AD | I_WSW_ | I_WSW_NUC_AD | Nuclear Production Plant |  |  |  | Null | Null |  |  |  | 85.56%
97 | Nuclear | Small Modular Reactor x 12 | 5000 | 570 | 2021 | 9.7524 | 2030.7524 | 40 | 9675.8543 | 15 | 0 | 0 | 167.77 | 0.75 | 10710 | 7.7 | 7.3 | 64.5435 | 0 | 0 | 0 | 0 | Small Modular Reactor x 12 | 5000 | 9675.8543 | 7.018% | 679.082 | 167.77 | 11.48% | 19.2574 | 0 | 187.0274 | 866.1094 | 85.56% | 115.5546 | na | 0 | 0 | 15 | 0% | 0 | 0 | 0 | 130.5546 | 0 | 130.5546 | 132 | Utah North | NUC_MD | I_UN_ | I_UN_NUC_MD | Nuclear Production Plant |  |  |  | Null | Null |  |  |  | 85.56%
133
| Wind | 2.0 MW turbine 38% CF WA,2021 | 1500 | 100 | 2017 | 5.0022 | 2022.0022 | 30 | 1799.7506 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 38% CF WA,2021 | 1500 | 1799.7506 | 7.067% | 127.1971 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 164.7627 | 35% | 53.7387 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 54.3117 |  | 54.3117 | 134 | [13 empty] | 38%
| Wind | 2.0 MW turbine 38% CF OR, 2021 | 1500 | 100 | 2017 | 5.0022 | 2022.0022 | 30 | 1773.9008 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 38% CF OR, 2021 | 1500 | 1773.9008 | 7.067% | 125.3702 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 162.9358 | 35% | 53.1428 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 53.7158 |  | 53.7158 | 135 | [13 empty] | 38%
| Wind | 2.0 MW turbine 38% CF ID, 2021 | 4500 | 100 | 2017 | 5.0022 | 2022.0022 | 30 | 1811.0329 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 38% CF ID, 2021 | 4500 | 1811.0329 | 7.067% | 127.9945 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 165.5601 | 35% | 53.9987 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 54.5717 |  | 54.5717 | 136 | [13 empty] | 38%
| Wind | 2.0 MW turbine 31% CF UT, 2021 | 4500 | 100 | 2017 | 5.0022 | 2022.0022 | 30 | 1735.3716 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 31% CF UT, 2021 | 4500 | 1735.3716 | 7.067% | 122.6471 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 160.2127 | 31% | 58.9972 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 59.5702 |  | 59.5702 | 137 | [13 empty] | 31%
| Wind | 3.3 MW turbine 43% CF WY, 2021 | 6500 | 100 | 2017 | 5.0022 | 2022.0022 | 30 | 1737.2477 | 0.65 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | 3.3 MW turbine 43% CF WY, 2021 | 6500 | 1737.2477 | 7.067% | 122.7797 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 160.3453 | 43% | 42.568 | na | 0 | 0 | 0.65 | 0% | 0 | 0.573 | 0 | 43.791 |  | 43.791 | 138 | [13 empty] | 43%
| Wind | 2.0 MW turbine 38% CF WA,2024 | 1500 | 100 | 2017 | 5.0022 | 2023 | 30 | 1799.7506 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 38% CF WA,2024 | 1500 | 1799.7506 | 7.067% | 127.1971 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 164.7627 | 38% | 49.4961 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 50.0691 |  | 50.0691 | 139 | [13 empty] | 38%
| Wind | 2.0 MW turbine 38% CF OR, 2024 | 1500 | 100 | 2017 | 5.0022 | 2023 | 30 | 1773.9008 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 38% CF OR, 2024 | 1500 | 1773.9008 | 7.067% | 125.3702 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 162.9358 | 38% | 48.9473 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 49.5203 |  | 49.5203 | 140 | [13 empty] | 38%
| Wind | 2.0 MW turbine 38% CF ID, 2024 | 4500 | 100 | 2017 | 5.0022 | 2023 | 30 | 1811.0329 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 38% CF ID, 2024 | 4500 | 1811.0329 | 7.067% | 127.9945 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 165.5601 | 38% | 49.7357 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 50.3087 |  | 50.3087 | 141 | [13 empty] | 38%
| Wind | 2.0 MW turbine 31% CF UT, 2024 | 4500 | 100 | 2017 | 5.0022 | 2023 | 30 | 1735.3716 | 0 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | 2.0 MW turbine 31% CF UT, 2024 | 4500 | 1735.3716 | 7.067% | 122.6471 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 160.2127 | 31% | 58.9972 | na | 0 | 0 | 0 | 0% | 0 | 0.573 | 0 | 59.5702 |  | 59.5702 | 142 | [13 empty] | 31%
| Wind | 3.3 MW turbine 43% CF WY, 2024 | 6500 | 100 | 2017 | 5.0022 | 2023 | 30 | 1737.2477 | 0.65 | 0 | 0 | 36.45 | 0.23128 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | 3.3 MW turbine 43% CF WY, 2024 | 6500 | 1737.2477 | 7.067% | 122.7797 | 36.45 | 3.061% | 1.1156 | 0 | 37.5656 | 160.3453 | 43% | 42.568 | na | 0 | 0 | 0.65 | 0% | 0 | 0.573 | 0 | 43.791 |  | 43.791 | 143 | [13 empty] | 43%
| Solar | PV Poly-Si Fixed Tilt 26.8% AC CF (1.35 MWdc/Mwac) UT, 2019 | 4500 | 50 | 2017 | 1.9998 | 2018.9998 | 25 | 1723.7488 | 0 | 0 | 0 | 18.45 | 0.12467 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Fixed Tilt 26.8% AC CF (1.35 MWdc/Mwac) UT, 2019 | 4500 | 1723.7488 | 6.512% | 112.2455 | 18.45 | 1.461% | 0.26953 | 0 | 18.7195 | 130.965 | 26.8% | 55.7849 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 56.3879 |  | 56.3879 | 144 | [13 empty] | 26.8%
| Solar | PV Poly-Si Single Tracking 31.1% AC CF (1.25 MWdc/Mwac) UT, 2019 | 4500 | 50 | 2017 | 1.9998 | 2018.9998 | 25 | 1822.4072 | 0 | 0 | 0 | 19.41 | 0.11851 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Single Tracking 31.1% AC CF (1.25 MWdc/Mwac) UT, 2019 | 4500 | 1822.4072 | 6.512% | 118.6698 | 19.41 | 1.461% | 0.28356 | 0 | 19.6936 | 138.3634 | 31.1% | 50.7875 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 51.3905 |  | 51.3905 | 145 | [13 empty] | 31.1%
| Solar | PV Poly-Si Fixed Tilt 24.9% AC CF (1.35 MWdc/Mwac) OR, 2019 | 4800 | 50 | 2017 | 2 | 2019 | 25 | 1761.8948 | 0 | 0 | 0 | 18.47 | 0.12451 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Fixed Tilt 24.9% AC CF (1.35 MWdc/Mwac) OR, 2019 | 4800 | 1761.8948 | 6.512% | 114.7294 | 18.47 | 1.461% | 0.26983 | 0 | 18.7398 | 133.4692 | 24.9% | 61.1896 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 61.7926 |  | 61.7926 | 146 | [13 empty] | 24.9%
| Solar | PV Poly-Si Single Tracking 28.8% AC CF (1.25 MWdc/Mwac) OR, 2019 | 4800 | 50 | 2017 | 2 | 2019 | 25 | 1856.7386 | 0 | 0 | 0 | 19.44 | 0.11833 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Single Tracking 28.8% AC CF (1.25 MWdc/Mwac) OR, 2019 | 4800 | 1856.7386 | 6.512% | 120.9054 | 19.44 | 1.461% | 0.284 | 0 | 19.724 | 140.6294 | 28.8% | 55.7416 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 56.3446 |  | 56.3446 | 147 | [13 empty] | 28.8%
| Solar | PV Poly-Si Fixed Tilt 26.8% AC CF (1.35 MWdc/Mwac) UT, 2023 | 4500 | 50 | 2017 | 1.9998 | 2023 | 25 | 1723.7488 | 0 | 0 | 0 | 18.45 | 0.12467 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Fixed Tilt 26.8% AC CF (1.35 MWdc/Mwac) UT, 2023 | 4500 | 1723.7488 | 6.911% | 119.1197 | 18.45 | 1.461% | 0.26953 | 0 | 18.7195 | 137.8393 | 26.8% | 58.713 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 59.316 |  | 59.316 | 148 | [13 empty] | 26.8%
| Solar | PV Poly-Si Single Tracking 31.1% AC CF (1.25 MWdc/Mwac) UT, 2023 | 4500 | 50 | 2017 | 1.9998 | 2023 | 25 | 1822.4072 | 0 | 0 | 0 | 19.41 | 0.11851 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Single Tracking 31.1% AC CF (1.25 MWdc/Mwac) UT, 2023 | 4500 | 1822.4072 | 6.911% | 125.9375 | 19.41 | 1.461% | 0.28356 | 0 | 19.6936 | 145.6311 | 31.1% | 53.4552 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 54.0582 |  | 54.0582 | 149 | [13 empty] | 31.1%
| Solar | PV Poly-Si Fixed Tilt 24.9% AC CF (1.35 MWdc/Mwac) OR, 2023 | 4800 | 50 | 2017 | 2 | 2023 | 25 | 1761.8948 | 0 | 0 | 0 | 18.47 | 0.12451 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Fixed Tilt 24.9% AC CF (1.35 MWdc/Mwac) OR, 2023 | 4800 | 1761.8948 | 6.911% | 121.7558 | 18.47 | 1.461% | 0.26983 | 0 | 18.7398 | 140.4956 | 24.9% | 64.4109 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 65.0139 |  | 65.0139 | 150 | [13 empty] | 24.9%
| Solar | PV Poly-Si Single Tracking 28.8% AC CF (1.25 MWdc/Mwac) OR, 2023 | 4800 | 50 | 2017 | 2 | 2023 | 25 | 1856.7386 | 0 | 0 | 0 | 19.44 | 0.11833 | n/a | Included with CF | 0 | n/a | n/a | n/a | n/a | n/a | PV Poly-Si Single Tracking 28.8% AC CF (1.25 MWdc/Mwac) OR, 2023 | 4800 | 1856.7386 | 6.911% | 128.31 | 19.44 | 1.461% | 0.284 | 0 | 19.724 | 148.034 | 28.8% | 58.6766 | na | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 59.2796 |  | 59.2796 | 151 | [13 empty] | 28.8%
| Solar | Not Used | [44 empty] | 152
| Solar | CSP Trough w Natural Gas | 4500 | 100 | 2017 | 5 | 2022 | 30 | 6447.5397 | 0 | 0 | 0 | 68.4642 | 0.39303 | 11750 | Included with CF | 0 | 725 | n/a | n/a | n/a | n/a | CSP Trough w Natural Gas |  | 6447.5397 | 6.682% | 430.8523 | 68.4642 | 0% | 0 | 17.8995 | 86.3638 | 517.2161 | 33% | 178.918 |  | 293.96 | 7.3669 | 0 | 0% | 0 | 0.603 | 0 | 186.8879 | 0 | 186.8879 | 153 |  | 25 |  | 60 | 50 | [8 empty] | 33%
| Solar | CSP Tower 24% CF | 4500 | 100 | 2017 | 5 | 2022 | 30 | 6141.4654 | 0 | 0 | 0 | 68.4642 | 0.39303 | n/a | Included with CF | 0 | 725 | n/a | n/a | n/a | n/a | CSP Tower 24% CF |  | 6141.4654 | 6.682% | 410.3991 | 68.4642 | 0% | 0 | 0 | 68.4642 | 478.8633 | 24% | 227.7698 |  | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 228.3728 | 0 | 228.3728 | 154 |  | 25 |  | 58 | 50 | [8 empty] | 24%
| Solar | CSP Tower Molten Salt 30% CF | 4500 | 100 | 2017 | 5 | 2022 | 30 | 7367.0328 | 0 | 0 | 0 | 68.4642 | 0.39303 | n/a | Included with CF | 0 | 750 | n/a | n/a | n/a | n/a | CSP Tower Molten Salt 30% CF |  | 7367.0328 | 6.682% | 492.2968 | 68.4642 | 0% | 0 | 0 | 68.4642 | 560.761 | 30% | 213.3794 |  | 0 | 0 | 0 | 0% | 0 | 0.603 | 0 | 213.9824 | 0 | 213.9824 | 155 |  | 25 |  | 58 | 51 | [8 empty] | 30%
156
[15 empty] | Average Full Load Heat Rate (HHV Btu/KWh)/Efficiency | [7 empty] | Brownfield Site | [23 empty] | 157
| Levelized $/Ton | [21 empty] | Dave Johnston | [23 empty] | 158
CO2 Price | 0 | [13 empty] | 9189 | [7 empty] | SCCT Aero x3 | 5050 | 1482.6307 | 7.871% | 116.6993 | 31.86 | 1.331% | 0.42396 | 53.2245 | 85.5085 | 202.2078 | 33% | 69.9487 | na | 289.04 | 26.5599 | 8.85 | 12.11% | 1.0717 | 0 | 0 | 106.4303 | 0 | 106.4303 | 159 | Dave Johnston | SC_Aero | I_DJ_ | I_DJ_SC_Aero | Single Cycle Combustion Turbine (SCCT) Aero
Notes | [14 empty] | 9032 | [7 empty] | Intercooled SCCT Aero x2 | 5050 | 1135.8112 | 7.871% | 89.4008 | 22.82 | 1.198% | 0.2733 | 52.3151 | 75.4084 | 164.8092 | 33% | 57.0116 | na | 289.04 | 26.1061 | 6.14 | 12.11% | 0.74351 | 0 | 0 | 90.0012 | 0 | 90.0012 | 160 | Dave Johnston | SC_ICAero | I_DJ_ | I_DJ_SC_ICAero | Intercooled SCCT Aero
Solar includes ITC benefit of 10% continuing after 2016 | [14 empty] | 9614 | [7 empty] | SCCT Frame "F" x1 | 5050 | 589.4961 | 7.373% | 43.4614 | 15.97 | 0.287% | 0.045829 | 55.6862 | 71.702 | 115.1634 | 33% | 39.8379 | na | 289.04 | 27.7883 | 6.61 | 13.92% | 0.91999 | 0 | 0 | 75.1562 | 0 | 75.1562 | 161 | Dave Johnston | SC_Frame | I_DJ_ | I_DJ_SC_Frame | Single Cycle Combustion Turbine (SCCT) Frame
Nuclear fuel cost is included in variable O&M | [14 empty] | 8286 | [7 empty] | IC Recips x 6 | 5050 | 1369.8564 | 7.871% | 107.8227 | 29.82 | 0.1435% | 0.042787 | 47.9942 | 77.8569 | 185.6797 | 33% | 64.2312 | na | 289.04 | 23.9499 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 96.3152 | 0 | 96.3152 | 162 | Dave Johnston | SC_ICE | I_DJ_ | I_DJ_SC_ICE | Internal Combustion Engines
Production Tax Credit (PTC) for wind, and geothermal shown as if tax credit were extended | [14 empty] | 6374 | [7 empty] | CCCT Dry "G/H", 1x1 | 5050 | 1519.0366 | 7.256% | 110.2257 | 24.74 | 0.153% | 0.037864 | 36.9195 | 61.6973 | 171.923 | 78% | 25.1614 | na | 289.04 | 18.4234 | 2.12 | 10.71% | 0.22712 | 0 | 0 | 45.932 | 0 | 45.932 | 163 | Dave Johnston | CC_GH_1x1 | I_DJ_ | I_DJ_CC_GH_1x1 | Combined Cycle Combustion Turbine (CCCT)
"NC" not calculated due to fuel costs not specified due to location specific | [14 empty] | 9172 | [7 empty] | CCCT Dry "G/H", DF, 1x1 | 5050 | 397.2825 | 7.256% | 28.828 | 5.39 | 0% | 0 | 53.126 | 58.516 | 87.344 | 12% | 83.0898 | na | 289.04 | 26.5107 | 0.15 | 0% | 0 | 0 | 0 | 109.7506 | 0 | 109.7506 | 164 | Dave Johnston | CC_GH_1x1_DF | I_DJ_ | I_DJ_CC_GH_1x1_DF | Combined Cycle Combustion Turbine (CCCT)
Capaciy Factor for natural gas resources from Preferred Portfolio new CCCT, peaker is based on EPA regulation max generation | [14 empty] | 6326 | [7 empty] | CCCT Dry "J/HA.02", 1x1 | 5050 | 1334.21 | 7.256% | 96.8141 | 21.26 | 0.153% | 0.032538 | 36.6414 | 57.934 | 154.7481 | 78% | 22.6478 | na | 289.04 | 18.2847 | 2.05 | 10.71% | 0.21962 | 0 | 0 | 43.2021 | 0 | 43.2021 | 165 | Dave Johnston | CC_J_1x1 | I_DJ_ | I_DJ_CC_J_1x1 | Combined Cycle Combustion Turbine (CCCT)
[15 empty] | 9211 | [7 empty] | CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 341.6069 | 7.256% | 24.788 | 4.86 | 0% | 0 | 53.3519 | 58.2119 | 82.9999 | 12% | 78.9573 | na | 289.04 | 26.6235 | 0.16 | 0% | 0 | 0 | 0 | 105.7408 | 0 | 105.7408 | 166 | Dave Johnston | CC_J_1x1_DF | I_DJ_ | I_DJ_CC_J_1x1_DF | Combined Cycle Combustion Turbine (CCCT)
[23 empty] | Hunter | [23 empty] | 167
[15 empty] | 9189 | [7 empty] | SCCT Aero x3 | 5050 | 1482.6307 | 7.871% | 116.6993 | 31.86 | 1.331% | 0.42396 | 13.9942 | 46.2781 | 162.9774 | 33% | 56.378 | na | 293.63 | 26.9817 | 8.85 | 12.11% | 1.0717 | 0 | 0 | 93.2813 | 0 | 93.2813 | 168 | Hunter | SC_Aero | I_HTR_ | I_HTR_SC_Aero | Single Cycle Combustion Turbine (SCCT) Aero
[15 empty] | 9032 | [7 empty] | Intercooled SCCT Aero x2 | 5050 | 1135.8112 | 7.871% | 89.4008 | 22.82 | 1.198% | 0.2733 | 13.7551 | 36.8484 | 126.2492 | 33% | 43.6727 | na | 293.63 | 26.5207 | 6.14 | 12.11% | 0.74351 | 0 | 0 | 77.0769 | 0 | 77.0769 | 169 | Hunter | SC_ICAero | I_HTR_ | I_HTR_SC_ICAero | Intercooled SCCT Aero
[15 empty] | 9614 | [7 empty] | SCCT Frame "F" x1 | 5050 | 589.4961 | 7.373% | 43.4614 | 15.97 | 0.287% | 0.045829 | 14.6414 | 30.6572 | 74.1186 | 33% | 25.6395 | na | 293.63 | 28.2296 | 6.61 | 13.92% | 0.91999 | 0 | 0 | 61.3991 | 0 | 61.3991 | 170 | Hunter | SC_Frame | I_HTR_ | I_HTR_SC_Frame | Single Cycle Combustion Turbine (SCCT) Frame
[15 empty] | 8286 | [7 empty] | IC Recips x 6 | 5050 | 1369.8564 | 7.871% | 107.8227 | 29.82 | 0.1435% | 0.042787 | 12.619 | 42.4818 | 150.3045 | 33% | 51.9941 | na | 293.63 | 24.3302 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 84.4584 | 0 | 84.4584 | 171 | Hunter | SC_ICE | I_HTR_ | I_HTR_SC_ICE | Internal Combustion Engines
[15 empty] | 6374 | [7 empty] | CCCT Dry "G/H", 1x1 | 5050 | 1519.0366 | 7.256% | 110.2257 | 24.74 | 0.153% | 0.037864 | 9.7071 | 34.485 | 144.7107 | 78% | 21.1788 | na | 293.63 | 18.716 | 2.12 | 10.71% | 0.22712 | 0 | 0 | 42.2419 | 0 | 42.2419 | 172 | Hunter | CC_GH_1x1 | I_HTR_ | I_HTR_CC_GH_1x1 | Combined Cycle Combustion Turbine (CCCT)
[15 empty] | 9172 | [7 empty] | CCCT Dry "G/H", DF, 1x1 | 5050 | 397.2825 | 7.256% | 28.828 | 5.39 | 0% | 0 | 13.9683 | 19.3583 | 48.1862 | 12% | 45.8393 | na | 293.63 | 26.9317 | 0.15 | 0% | 0 | 0 | 0 | 72.921 | 0 | 72.921 | 173 | Hunter | CC_GH_1x1_DF | I_HTR_ | I_HTR_CC_GH_1x1_DF | Combined Cycle Combustion Turbine (CCCT)
[15 empty] | 6326 | [7 empty] | CCCT Dry "J/HA.02", 1x1 | 5050 | 1334.21 | 7.256% | 96.8141 | 21.26 | 0.153% | 0.032538 | 9.634 | 30.9266 | 127.7407 | 78% | 18.6952 | na | 293.63 | 18.575 | 2.05 | 10.71% | 0.21962 | 0 | 0 | 39.5399 | 0 | 39.5399 | 174 | Hunter | CC_J_1x1 | I_HTR_ | I_HTR_CC_J_1x1 | Combined Cycle Combustion Turbine (CCCT)
[15 empty] | 9211 | [7 empty] | CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 341.6069 | 7.256% | 24.788 | 4.86 | 0% | 0 | 14.0277 | 18.8877 | 43.6757 | 12% | 41.5484 | na | 293.63 | 27.0463 | 0.16 | 0% | 0 | 0 | 0 | 68.7546 | 0 | 68.7546 | 175 | Hunter | CC_J_1x1_DF | I_HTR_ | I_HTR_CC_J_1x1_DF | Combined Cycle Combustion Turbine (CCCT)
[23 empty] | Huntington | [23 empty] | 176
[15 empty] | 9189 | [7 empty] | SCCT Aero x3 | 5050 | 1482.6307 | 7.871% | 116.6993 | 31.86 | 1.331% | 0.42396 | 13.9942 | 46.2781 | 162.9774 | 33% | 56.378 | na | 293.63 | 26.9817 | 8.85 | 12.11% | 1.0717 | 0 | 0 | 93.2813 | 0 | 93.2813 | 177 | Huntington | SC_Aero | I_HTN_ | I_HTN_SC_Aero | Single Cycle Combustion Turbine (SCCT) Aero
[15 empty] | 9032 | [7 empty] | Intercooled SCCT Aero x2 | 5050 | 1135.8112 | 7.871% | 89.4008 | 22.82 | 1.198% | 0.2733 | 13.7551 | 36.8484 | 126.2492 | 33% | 43.6727 | na | 293.63 | 26.5207 | 6.14 | 12.11% | 0.74351 | 0 | 0 | 77.0769 | 0 | 77.0769 | 178 | Huntington | SC_ICAero | I_HTN_ | I_HTN_SC_ICAero | Intercooled SCCT Aero
[15 empty] | 9614 | [7 empty] | SCCT Frame "F" x1 | 5050 | 589.4961 | 7.373% | 43.4614 | 15.97 | 0.287% | 0.045829 | 14.6414 | 30.6572 | 74.1186 | 33% | 25.6395 | na | 293.63 | 28.2296 | 6.61 | 13.92% | 0.91999 | 0 | 0 | 61.3991 | 0 | 61.3991 | 179 | Huntington | SC_Frame | I_HTN_ | I_HTN_SC_Frame | Single Cycle Combustion Turbine (SCCT) Frame
[15 empty] | 8286 | [7 empty] | IC Recips x 6 | 5050 | 1369.8564 | 7.871% | 107.8227 | 29.82 | 0.1435% | 0.042787 | 12.619 | 42.4818 | 150.3045 | 33% | 51.9941 | na | 293.63 | 24.3302 | 7.45 | 9.183% | 0.68414 | 0 | 0 | 84.4584 | 0 | 84.4584 | 180 | Huntington | SC_ICE | I_HTN_ | I_HTN_SC_ICE | Internal Combustion Engines
[15 empty] | 6374 | [7 empty] | CCCT Dry "G/H", 1x1 | 5050 | 1519.0366 | 7.256% | 110.2257 | 24.74 | 0.153% | 0.037864 | 9.7071 | 34.485 | 144.7107 | 78% | 21.1788 | na | 293.63 | 18.716 | 2.12 | 10.71% | 0.22712 | 0 | 0 | 42.2419 | 0 | 42.2419 | 181 | Huntington | CC_GH_1x1 | I_HTN_ | I_HTN_CC_GH_1x1 | Combined Cycle Combustion Turbine (CCCT)
[15 empty] | 9172 | [7 empty] | CCCT Dry "G/H", DF, 1x1 | 5050 | 397.2825 | 7.256% | 28.828 | 5.39 | 0% | 0 | 13.9683 | 19.3583 | 48.1862 | 12% | 45.8393 | na | 293.63 | 26.9317 | 0.15 | 0% | 0 | 0 | 0 | 72.921 | 0 | 72.921 | 182 | Huntington | CC_GH_1x1_DF | I_HTN_ | I_HTN_CC_GH_1x1_DF | Combined Cycle Combustion Turbine (CCCT)
[15 empty] | 6365 | [7 empty] | CCCT Dry "G/H", 2x1 | 5050 | 1163.2405 | 7.256% | 84.4081 | 16.63 | 0.153% | 0.025452 | 9.6934 | 26.3489 | 110.757 | 78% | 16.2096 | na | 293.63 | 18.6895 | 2.01 | 11.33% | 0.22764 | 0 | 0 | 37.1368 | 0 | 37.1368 | 183 | Huntington | CC_GH_2x1 | I_HTN_ | I_HTN_CC_GH_2x1 | Combined Cycle Combustion Turbine (CCCT)
[15 empty] | 9141 | [7 empty] | CCCT Dry "G/H", DF, 2x1 | 5050 | 321.9656 | 7.256% | 23.3628 | 4.44 | 0% | 0 | 13.9211 | 18.3611 | 41.7238 | 12% | 39.6916 | na | 293.63 | 26.8407 | 0.16 | 0% | 0 | 0 | 0 | 66.6923 | 0 | 66.6923 | 184 | Huntington | CC_GH_2x1_DF | I_HTN_ | I_HTN_CC_GH_2x1_DF | Combined Cycle Combustion Turbine (CCCT)
[15 empty] | 6326 | [7 empty] | CCCT Dry "J/HA.02", 1x1 | 5050 | 1334.21 | 7.256% | 96.8141 | 21.26 | 0.153% | 0.032538 | 9.634 | 30.9266 | 127.7407 | 78% | 18.6952 | na | 293.63 | 18.575 | 2.05 | 10.71% | 0.21962 | 0 | 0 | 39.5399 | 0 | 39.5399 | 185 | Huntington | CC_J_1x1 | I_HTN_ | I_HTN_CC_J_1x1 | Combined Cycle Combustion Turbine (CCCT)
[15 empty] | 9211 | [7 empty] | CCCT Dry "J/HA.02", DF, 1x1 | 5050 | 341.6069 | 7.256% | 24.788 | 4.86 | 0% | 0 | 14.0277 | 18.8877 | 43.6757 | 12% | 41.5484 | na | 293.63 | 27.0463 | 0.16 | 0% | 0 | 0 | 0 | 68.7546 | 0 | 68.7546 | 186 | Huntington | CC_J_1x1_DF | I_HTN_ | I_HTN_CC_J_1x1_DF | Combined Cycle Combustion Turbine (CCCT)
[23 empty] | Jim Bridger | [23 empty] | 187
[15 empty] | 9195 | [7 empty] | SCCT Aero x3 | 6500 | 1608.4033 | 7.871% | 126.599 | 34.56 | 1.331% | 0.45989 | 9.1121 | 44.132 | 170.7309 | 33% | 59.0601 | na | 288.77 | 26.5524 | 9.6 | 12.11% | 1.1625 | 0 | 0 | 96.375 | 0 | 96.375 | 188 | Jim Bridger | SC_Aero | I_JB_ | I_JB_SC_Aero | Single Cycle Combustion Turbine (SCCT) Aero
[15 empty] | 9003 | [7 empty] | Intercooled SCCT Aero x2 | 6500 | 1194.5446 | 7.871% | 94.0238 | 24 | 1.198% | 0.28743 | 8.9218 | 33.2092 | 127.233 | 33% | 44.0131 | na | 288.77 | 25.998 | 6.45 | 12.11% | 0.78105 | 0 | 0 | 77.2421 | 0 | 77.2421 | 189 | Jim Bridger | SC_ICAero | I_JB_ | I_JB_SC_ICAero | Intercooled SCCT Aero
[15 empty] | 9605 | [7 empty] | SCCT Frame "F" x1 | 6500 | 620.8085 | 7.373% | 45.7699 | 16.81 | 0.287% | 0.04824 | 9.5184 | 26.3766 | 72.1465 | 33% | 24.9573 | na | 288.77 | 27.7364 | 6.96 | 13.92% | 0.9687 | 0 | 0 | 60.6224 | 0 | 60.6224 | 190 | Jim Bridger | SC_Frame | I_JB_ | I_JB_SC_Frame | Single Cycle Combustion Turbine (SCCT) Frame
[15 empty] | 8377 | [7 empty] | IC Recips x 6 | 6500 | 1426.1534 | 7.871% | 112.2539 | 31.04 | 0.1435% | 0.044538 | 8.3015 | 39.386 | 151.6399 | 33% | 52.456 | na | 288.77 | 24.1903 | 7.75 | 9.183% | 0.71169 | 0 | 0 | 85.108 | 0 | 85.108 | 191 | Jim Bridger | SC_ICE | I_JB_ | I_JB_SC_ICE | Internal Combustion Engines
[15 empty] | 6395 | [7 empty] | CCCT Dry "G/H", 1x1 | 6500 | 1608.8286 | 7.256% | 116.7412 | 26.2 | 0.153% | 0.040098 | 6.3373 | 32.5774 | 149.3187 | 78% | 21.8532 | na | 288.77 | 18.4668 | 2.25 | 10.71% | 0.24105 | 0 | 0 | 42.8111 | 0 | 42.8111 | 192 | Jim Bridger | CC_GH_1x1 | I_JB_ | I_JB_CC_GH_1x1 | Combined Cycle Combustion Turbine (CCCT)
[15 empty] | 9524 | [7 empty] | CCCT Dry "G/H", DF, 1x1 | 6500 | 397.392 | 7.256% | 28.8359 | 5.39 | 0% | 0 | 9.4381 | 14.8281 | 43.664 | 12% | 41.5373 | na | 288.77 | 27.5025 | 0.15 | 0% | 0 | 0 | 0 | 69.1898 | 0 | 69.1898 | 193 | Jim Bridger | CC_GH_1x1_DF | I_JB_ | I_JB_CC_GH_1x1_DF | Combined Cycle Combustion Turbine (CCCT)
[15 empty] | 6336 | [7 empty] | CCCT Dry "J/HA.02", 1x1 | 6500 | 1401.3397 | 7.256% | 101.6852 | 22.33 | 0.153% | 0.034175 | 6.2789 | 28.643 | 130.3283 | 78% | 19.0739 | na | 288.77 | 18.2965 | 2.15 | 10.71% | 0.23033 | 0 | 0 | 39.7507 | 0 | 39.7507 | 194 | Jim Bridger | CC_J_1x1 | I_JB_ | I_JB_CC_J_1x1 | Combined Cycle Combustion Turbine (CCCT)
[15 empty] | 9524 | [7 empty] | CCCT Dry "J/HA.02", DF, 1x1 | 6500 | 341.6006 | 7.256% | 24.7875 | 4.86 | 0% | 0 | 9.4381 | 14.2981 | 39.0856 | 12% | 37.1819 | na | 288.77 | 27.5025 | 0.16 | 0% | 0 | 0 | 0 | 64.8444 | 0 | 64.8444 | 195 | Jim Bridger | CC_J_1x1_DF | I_JB_ | I_JB_CC_J_1x1_DF | Combined Cycle Combustion Turbine (CCCT)
[23 empty] | Naughton | [23 empty] | 196
[15 empty] | 9195 | [7 empty] | SCCT Aero x3 | 6500 | 1608.4033 | 7.871% | 126.599 | 34.56 | 1.331% | 0.45989 | 14.0033 | 49.0232 | 175.6222 | 33% | 60.7521 | na | 293.63 | 26.9993 | 9.6 | 12.11% | 1.1625 | 0 | 0 | 98.5139 | 0 | 98.5139 | 197 | Naughton | SC_Aero | I_NTN_ | I_NTN_SC_Aero | Single Cycle Combustion Turbine (SCCT) Aero
[15 empty] | 9003 | [7 empty] | Intercooled SCCT Aero x2 | 6500 | 1194.5446 | 7.871% | 94.0238 | 24 | 1.198% | 0.28743 | 13.7109 | 37.9983 | 132.0221 | 33% | 45.6697 | na | 293.63 | 26.4355 | 6.45 | 12.11% | 0.78105 | 0 | 0 | 79.3363 | 0 | 79.3363 | 198 | Naughton | SC_ICAero | I_NTN_ | I_NTN_SC_ICAero | Intercooled SCCT Aero
[15 empty] | 9605 | [7 empty] | SCCT Frame "F" x1 | 6500 | 620.8085 | 7.373% | 45.7699 | 16.81 | 0.287% | 0.04824 | 14.6277 | 31.4859 | 77.2559 | 33% | 26.7247 | na | 293.63 | 28.2032 | 6.96 | 13.92% | 0.9687 | 0 | 0 | 62.8566 | 0 | 62.8566 | 199 | Naughton | SC_Frame | I_NTN_ | I_NTN_SC_Frame | Single Cycle Combustion Turbine (SCCT) Frame
[15 empty] | 8377 | [7 empty] | IC Recips x 6 | 6500 | 1426.1534 | 7.871% | 112.2539 | 31.04 | 0.1435% | 0.044538 | 12.7576 | 43.8421 | 156.096 | 33% | 53.9975 | na | 293.63 | 24.5974 | 7.75 | 9.183% | 0.71169 | 0 | 0 | 87.0566 | 0 | 87.0566 | 200 | Naughton | SC_ICE | I_NTN_ | I_NTN_SC_ICE | Internal Combustion Engines
[15 empty] | 6336 | [7 empty] | CCCT Dry "J/HA.02", 1x1 | 6500 | 1401.3397 | 7.256% | 101.6852 | 22.33 | 0.153% | 0.034175 | 9.6493 | 32.0134 | 133.6987 | 78% | 19.5672 | na | 293.63 | 18.6044 | 2.15 | 10.71% | 0.23033 | 0 | 0 | 40.5519 | 0 | 40.5519 | 203 | Naughton | CC_J_1x1 | I_NTN_ | I_NTN_CC_J_1x1 | Combined Cycle Combustion Turbine (CCCT)
[15 empty] | 9524 | [7 empty] | CCCT Dry "J/HA.02", DF, 1x1 | 6500 | 341.6006 | 7.256% | 24.7875 | 4.86 | 0% | 0 | 14.5043 | 19.3643 | 44.1519 | 12% | 42.0014 | na | 293.63 | 27.9653 | 0.16 | 0% | 0 | 0 | 0 | 70.1267 | 0 | 70.1267 | 204 | Naughton | CC_J_1x1_DF | I_NTN_ | I_NTN_CC_J_1x1_DF | Combined Cycle Combustion Turbine (CCCT)
[23 empty] | Wyodak | [23 empty] | 205
[15 empty] | 9195 | [7 empty] | SCCT Aero x3 | 6500 | 1608.4033 | 7.871% | 126.599 | 34.56 | 1.331% | 0.45989 | 53.2593 | 88.2792 | 214.8781 | 33% | 74.3317 | na | 291.24 | 26.7795 | 9.6 | 12.11% | 1.1625 | 0 | 0 | 111.8737 | 0 | 111.8737 | 206 | Wyodak | SC_Aero | I_WYD_ | I_WYD_SC_Aero | Single Cycle Combustion Turbine (SCCT) Aero
[15 empty] | 9003 | [7 empty] | Intercooled SCCT Aero x2 | 6500 | 1194.5446 | 7.871% | 94.0238 | 24 | 1.198% | 0.28743 | 52.1472 | 76.4346 | 170.4584 | 33% | 58.9658 | na | 291.24 | 26.2203 | 6.45 | 12.11% | 0.78105 | 0 | 0 | 92.4172 | 0 | 92.4172 | 207 | Wyodak | SC_ICAero | I_WYD_ | I_WYD_SC_ICAero | Intercooled SCCT Aero
[15 empty] | 9605 | [7 empty] | SCCT Frame "F" x1 | 6500 | 620.8085 | 7.373% | 45.7699 | 16.81 | 0.287% | 0.04824 | 55.6341 | 72.4923 | 118.2622 | 33% | 40.9099 | na | 291.24 | 27.9736 | 6.96 | 13.92% | 0.9687 | 0 | 0 | 76.8122 | 0 | 76.8122 | 208 | Wyodak | SC_Frame | I_WYD_ | I_WYD_SC_Frame | Single Cycle Combustion Turbine (SCCT) Frame
[15 empty] | 8377 | [7 empty] | IC Recips x 6 | 6500 | 1426.1534 | 7.871% | 112.2539 | 31.04 | 0.1435% | 0.044538 | 48.5212 | 79.6058 | 191.8597 | 33% | 66.3691 | na | 291.24 | 24.3972 | 7.75 | 9.183% | 0.71169 | 0 | 0 | 99.2279 | 0 | 99.2279 | 209 | Wyodak | SC_ICE | I_WYD_ | I_WYD_SC_ICE | Internal Combustion Engines

## Database (Storage)
INPUTS
Description |  | Resource Characteristics |  |  | Costs |  |  | Operating Characteristics
Fuel | Resource | Elevation (AFSL) | Net Capacity (MW) | Technical Life (years) | Base Capital ($/KW) | Var O&M ($/MWh) | Fixed O&M ($/kW-yr) with capitalized O&M | Hours Day | System Efficiency (AC out/AC in) | Maximum Annual Generation (MWh/yr) | Reservoir Size | Reserve | Max Pump
Storage | Lithium Ion Battery (4 MWh/day) | 5000 | 1 | 20 | 4332.1775 | 0 | 28.44 | 4 | 0.85 | 736 | 0.0047059 | 1 | 0.29412
Storage | Flow (4 MWh/day) | 5000 | 1 | 20 | 4867.0169 | 0 | 33.5 | 4 | 0.72 | 2000 | 0.0055556 | 1 | 0.34722

## Energy Stor Cost Escalation
|  |  |  | Lithium Ion Battery (4 MWh/day) |  |  | Flow (4 MWh/day)
Capital Cost (1MW/4hr, 2016 $) |  |  | Name | Year | Capital Cost | Name | Year | Capital Cost
Lithium Ion |  |  | Lithium Ion | 2016 | 4332.1775 | Vanadium Flow | 2016 | 4867.0169
Vanadium Flow |  |  | Lithium Ion | 2017 | 3908.0731 | Vanadium Flow | 2017 | 4603.5825
|  |  | Lithium Ion | 2018 | 3550.6518 | Vanadium Flow | 2018 | 4392.4698
| Lithium | Flow | Lithium Ion | 2019 | 3273.6218 | Vanadium Flow | 2019 | 4225.2704
Year | Escalation | Escalation | Lithium Ion | 2020 | 3042.9741 | Vanadium Flow | 2020 | 4076.9932
1 | -9.79% | -5.413% | Lithium Ion | 2021 | 2859.5489 | Vanadium Flow | 2021 | 3971.2143
2 | -9.146% | -4.586% | Lithium Ion | 2022 | 2721.1263 | Vanadium Flow | 2022 | 3903.379
3 | -7.802% | -3.806% | Lithium Ion | 2023 | 2602.2982 | Vanadium Flow | 2023 | 3856.2049
4 | -7.046% | -3.509% | Lithium Ion | 2024 | 2511.8856 | Vanadium Flow | 2024 | 3816.5341
5 | -6.028% | -2.595% | Lithium Ion | 2025 | 2450.3398 | Vanadium Flow | 2025 | 3788.9258
6 | -4.841% | -1.708% | Lithium Ion | 2026 | 2414.1113 | Vanadium Flow | 2026 | 3781.5386
7 | -4.367% | -1.209%
8 | -3.474% | -1.029%
9 | -2.45% | -0.7234%
10 | -1.479% | -0.195%

## LCF
2017 Integrated Resource Plan
Resource Lives
Levelized Fixed Charge Percentages
CRF
1st Year
[9 empty] | Nominal | Real
|  | Category | Notes | Asset Weighting | Tax Life Weighting | Book Life | Tax Life | ITC | LFC | LFC 3/
1 | Transmission (higher than 69 KV) | Transmission |  |  | - | 58 | 15-yr | 0% | 8.957% | 6.348%
2 | Transmission (69 KV & Lower) | Transmission |  |  | - | 58 | 20-yr | 0% | 9.256% | 6.56%
3 | Coal (Pulverized) | Coal
4 | Plant without Air PCE |  |  | 80% | 88% | 40 | 20-yr | 0% | 9.647% | 7.256%
5 | Air Pollution Control Equipment | 4/ |  | 20% | 12% | 40 | CAI7 | 0% | 9.053% | 6.809% | 2/
6 | Coal (Pulverized) Weighted |  |  | 100% | 100% | - | - |  |  | 7.203%
7
8 | Coal (Pulverized) with CCS | Coal
9 | Power Block |  |  | 63% | 77.8% | 40 | 20-yr | 0% | 9.647% | 7.256%
10 | CCS (Carbon Capture & Sequestration) |  |  | 37% | 22.2% | 40 | CAI7 | 0% | 9.053% | 6.809%
11 | Coal (Pulverized) with CCS Weighted |  |  | 100% | 100% |  |  |  |  | 7.157%
12
13 | CCS Retrofit Existing Coal Plant (Bridger 1 & 2) | Coal | Inservice Unit 1 (1974), Unit 2 (1975), Unit 3 (1976), Unit 4 (1979)
14 | Power Block |  |  | 63% | 77.8% | 40 | 20-yr | 0% | 9.647% | 7.256%
15 | CCS (Carbon Capture & Sequestration) |  |  | 37% | 22.2% | 40 | CAI5 | 0% | 8.923% | 6.712%
16 | Total |  |  | 100% | 100% |  |  |  |  | 7.135%
17
18 | CCS Retrofit Existing Coal Plant (Hunter 3) | Coal | Inservice Unit 3 (1983)
19 | Power Block |  |  | 63% | 77.8% | 40 | 20-yr | 0% | 9.647% | 7.256%
20 | CCS (Carbon Capture & Sequestration) |  |  | 37% | 22.2% | 40 | CAI7 | 0% | 9.053% | 6.809%
21 | Total |  |  | 100% | 100% |  |  |  |  | 7.157%
22
23 | Internal Gasification Combined Cycle (w/o CCS) | Coal
24 | IGCC Power Block (37%) |  |  | 37% | 37% | 40 | 20-yr | 0% | 9.647% | 7.256%
25 | IGCC Gasifier (63%) |  |  | 63% | 63% | 40 | 10-yr | 0% | 8.811% | 6.627% | 1/
26 | IGCC (Power Block & Gasifier weighted) |  |  | 100% | 100% | - | - |  |  | 6.86%
27
28 | Internal Gasification Combined Cycle (w/ CCS) | Coal
29 | IGCC Power Block (29%) |  |  | 28.86% | 32.12% | 40 | 20-yr | 0% | 9.647% | 7.256%
30 | IGCC Gasifier (49%) |  |  | 49.14% | 54.68% | 40 | 10-yr | 0% | 8.811% | 6.627%
31 | IGCC CCS (22%) |  |  | 22% | 13.2% | 40 | CAI7 | 0% | 9.053% | 6.809%
32 | IGCC (Power Block, Gasifier, CCS weighted) |  |  | 100% | 100% |  |  |  |  | 6.853%
33
34 | Combined Cycle Combustion Turbine (CCCT) | Natural Gas |  |  | - | 40 | 20-yr | 0% | 9.647% | 7.256%
35 | Single Cycle Combustion Turbine (SCCT) Frame | Natural Gas |  |  | - | 35 | 15-yr | 0% | 9.579% | 7.373%
36 | Single Cycle Combustion Turbine (SCCT) Aero | Natural Gas |  |  | - | 30 | 15-yr | 0% | 9.959% | 7.871%
37 | Intercooled SCCT Aero | Natural Gas |  |  | - | 30 | 15-yr | 0% | 9.959% | 7.871%
38 | Internal Combustion Engines | Natural Gas |  |  | - | 30 | 15-yr | 0% | 9.959% | 7.871%
39 | Fuel Cells | Natural Gas |  |  | - | 35 | 5-yr | 0% | 8.608% | 6.625%
40 | Microturbines | Natural Gas |  |  | - | 15 | 5-yr | 0 | 11.94% | 10.46%
41
42 | Geothermal | Renewable |  |  | - | 40 | 5-yr | 0% | 8.391% | 6.311%
43 | Wind | Renewable |  |  | - | 30 | 5-yr | 0% | 8.942% | 7.067%
44 | Biomass | Renewable |  |  | - | 30 | 5-yr | 0 | 0.089424 | 7.067%
45 | Hydrokinetic (Wave) | Renewable |  |  | - | 20 | 7-yr | 0 | 0.1058 | 8.918%
46
47 | Solar Qualifies for 30% ITC
48 | Photovoltaic (Utility) 30% ITC | Solar | PV thin film 21% CF; PV SI Fixed Tilt 25% CF; PV SI Single Tracking 22 CF; |  | - | 25 | 5-yr | 30% | 8.124% | 6.618%
49 | Photovoltaic (Utility) 10% ITC | Solar | PV thin film 21% CF; PV SI Fixed Tilt 25% CF; PV SI Single Tracking 22 CF; |  | - | 25 | 5-yr | 10% | 9.023% | 7.35%
50 | Concentrating Solar Power Tower | Solar | 24% CF |  | - | 30 | 5-yr | 10% | 8.455% | 6.682%
51 | Concentrating Solar Power Tower (Thermal Storage) | Solar | Molten Salt 30% CF |  | - | 30 | 5-yr | 10% | 8.455% | 6.682%
52 | Concentrating Solar Power with Natural Gas (Thermal Storage) |  | NG Backup
53 | Solar | Solar |  | 80% | 41.67% | 30 | 5-yr | 0.1 | 8.455% | 6.682%
54 | Natural Gas Backup | Natural Gas |  | 20% | 58.33% | 30 | 15-yr | 0 | 9.959% | 7.871%
55 | Total Natural Gas Concentrating Solar |  | use Natural Gas factor operates more than solar | 1 | 1 |  |  |  |  | 7.871%
56
57 | Pumped Storage | Storage |  |  | - | 60 | 20-yr | 0% | 9.239% | 6.517%
58 | Battery Storage | Storage | Lithium Ion; Sodium-Sulfur; Vanadium RedOx; |  | - | 20 | 20-yr | 0% | 11.96% | 10.08%
59 | Fly Wheel | Storage |  |  | - | 30 | 20-yr | 0% | 10.3% | 8.142%
60 | Compressed Air Energy Storage (CAES) | Storage |  |  | - | 30 | 15-yr | 0% | 9.959% | 7.871%
61 | Nuclear Production Plant | Nuclear | Advanced Fusion; Modular Reactor |  | - | 40 | 15-yr | 0% | 9.331% | 7.018%
62 | Nuclear Fuel Assemblies | Nuclear |  |  | - | 40 | 5-yr | 0% | 8.391% | 6.311%
63
64 | CHP-Reciprocating Engine | Customer owned |  |  | - | 20 | 20-yr | 0% | 0.11958 | 10.08%
65 | CHP - Gas Turbine | Customer owned |  |  | - | 20 | 20-yr | 0% | 0.11958 | 10.08%
66 | CHP - Microturbine | Customer owned |  |  | - | 15 | 5-yr | 0% | 0.11942 | 10.46%
67 | CHP - Fuel Cell | Customer owned |  |  | - | 10 | 5-yr | 0% | 0.15322 | 14.01%
68 | CHP - Commercial Biomass, Anaerobic Digester | Customer owned |  |  | - | 15 | 5-yr | 0% | 0.11942 | 10.46%
69 | CHP - Industrial Biomass Waste | Customer owned |  |  | - | 15 | 5-yr | 0 | 0.11942 | 10.46%
70 | Solar - Rooftop Photovoltaic | Customer owned |  |  | - | 25 | 5-yr | 0 | 0.094722 | 7.716%
71 | Solar - Water Heaters | Customer owned |  |  | - | 15 | 5-yr | 0 | 0.11942 | 10.46%
72 | Solar - Attic Fans | Customer owned |  |  | - | 10 | 5-yr | 0 | 0.15322 | 14.01%
73 | Solar (2019) | Solar |  |  |  | 25 | 5-yr | 30% |  | 6.512%
74 | Solar (2023) | Solar |  |  |  | 25 | 5-yr | 22% |  | 6.911%
75
76
77
78
79
80
81
82
83
84
85
86
| Discount rate = | 0.0657
| Esc = | 0.0222
| General Property Tax Rate = % of net plant | 0.012
1/ tax department 10 Year tax life on gasification
2/ air pollution control percent of capital investment from Generation
3/ Input to IRP System Optimizer Model
4/ 60% of Pollution Control equipment qualifies afor 84 month tax treatment
| Tax % Pollution Control qualifies for 60 month - 84 month | 0.6
| Solar Concentrating Natural Gas | Generation
| Solar | 0.25
| Natural Gas | 0.35
| Total (up to 60%) | 0.6

## Inputs
Inputs
Vintage | 2016
Item | Notes | Worksheet Inputs | ID
Natural Gas | cents mmbtu
Utah North |  | 293.96 | I_UN_
Utah South |  | 294.97 | I_US_
Pacific Northwest |  | 294.97 | I_PNC_
Southern Oregon - California |  | 293.35 | I_SO_
WY-NE |  | 289.04 | I_WYNE_
WY-SW |  | 289.01 | I_WSW_
Dave Johnston |  | 289.04 | I_DJ_
Hunter |  | 293.63 | I_HTR_
Huntington |  | 293.63 | I_HTN_
Jim Bridger |  | 288.77 | I_JB_
Naughton |  | 293.63 | I_NTN_
Wyodak |  | 291.24 | I_WYD_
Walla Walla |  | 294.97 | I_WW_
Nuclear Fuel | included in VOM
PTC - Geothermal |  | 12.4 | Geothermal
PTC - Wind |  | 12.4 | Wind
PTC_Wind_40% |  | 40% | Wind40
PTC_Wind_100% |  | 100% | Wind100
Green Tag |  | 0
Wind Integration |  | 0.573 | Wind Integration
Solar Integration | assumed to be 25% of wind | 0.603 | Solar Integration
CO2 Price |  | 0
Tax Rate |  | 37.95% | Tax
CAES Storage Efficiency |  | 50%
CSP Trough with Nat Gas (Gas Trans) |  | 17.8995
1 |  | 1 | Unit
0 |  | 0 | Null

## Other Inputs
SO Name | VOM Premium % | FOM Premium % | SO Name | Fixed Gas Transport | Var O&M ($/MWh) | Fixed O&M ($/KW-year) | Heat Rate |  |  | Gas-Fueled Resource Type | Brownfield Gas Plant Multiplier
CAES | 5.456% | 0% | I_DJ_CC_GH_1x1 | 36.9195 | 2.12 | 24.74 | 6374 | Resource Type | Technology | (SC, CC) | (BF owners/GF owners)
CC_GH_1x1 | 10.71% | 0.153% | I_DJ_CC_GH_1x1_DF | 53.126 | 0.15 | 5.39 | 9172 | SC_Aero | SCCT Aero x 3 | SC | 0.88891
CC_GH_1x1_DF | 0% | 0% | I_DJ_CC_GH_2x1 | 36.8673 | 2.01 | 16.63 | 6365 | SC_ICAero | Intercooled SSCT Aero x 1 | SC | 0.90211
CC_GH_2x1 | 11.33% | 0.153% | I_DJ_CC_GH_2x1_DF | 52.9465 | 0.16 | 4.44 | 9141 | SC_Frame | SCCT Frame "F" x 1 | SC | 0.84022
CC_GH_2x1_DF | 0% | 0% | I_DJ_CC_J_1x1 | 36.6414 | 2.05 | 21.26 | 6326 | SC_ICE | IC Recips x 6 | SC | 0.87117
CC_J_1x1 | 10.71% | 0.153% | I_DJ_CC_J_1x1_DF | 53.3519 | 0.16 | 4.86 | 9211 | CC_GH_1x1 | CCCT Dry "G/H", 1x1 | CC | 0.89706
CC_J_1x1_DF | 0% | 0% | I_DJ_CC_J_2x1 | 36.5893 | 1.95 | 14.45 | 6317 | CC_GH_2x1 | CCCT Dry "G/H", DF, 2x1 | CC | 0.9251
CC_J_2x1 | 11.33% | 0.153% | I_DJ_CC_J_2x1_DF | 53.045 | 0.16 | 4.05 | 9158 | CC_GH_1x1_DF | CCCT Dry "G/H", 1x1 | CC | 0.89706
CC_J_2x1_DF | 0% | 0% | I_DJ_SC_Aero | 53.2245 | 8.85 | 31.86 | 9189 | CC_GH_2x1_DF | CCCT Dry "G/H", DF, 2x1 | CC | 0.9251
GEO_B35 | 0% | 0.9183% | I_DJ_SC_Frame | 55.6862 | 6.61 | 15.97 | 9614 | CC_J_1x1 | CCCT Dry "J/HA.02", 1x1 | CC | 0.90355
GEO_PPA | 0% | 0% | I_DJ_SC_ICAero | 52.3151 | 6.14 | 22.82 | 9032 | CC_J_2x1 | CCCT Dry "J/HA.02", DF, 2X1 | CC | 0.93005
NUC_AD | 0% | 5.816% | I_DJ_SC_ICE | 47.9942 | 7.45 | 29.82 | 8286 | CC_J_1x1_DF | CCCT Dry "J/HA.02", 1x1 | CC | 0.90355
NUC_MD | 0% | 11.48% | I_DJ_WD | 0 | 0.65 | 36.45 | n/a | CC_J_2x1_DF | CCCT Dry "J/HA.02", DF, 2X1 | CC | 0.93005
PUMP | 0% | 0% | I_GO_CC_GH_1x1 | 63.4837 | 2.12 | 24.74 | 6374
PV50FT | 0% | 1.461% | I_GO_CC_GH_1x1_DF | 91.3512 | 0.15 | 5.39 | 9172
PV50ST | 0% | 1.461% | I_GO_CC_GH_2x1 | 63.3941 | 2.01 | 16.63 | 6365
SC_Aero | 12.11% | 1.331% | I_GO_CC_GH_2x1_DF | 91.0424 | 0.16 | 4.44 | 9141
SC_Frame | 13.92% | 0.287% | I_GO_CC_J_1x1 | 63.0056 | 2.05 | 21.26 | 6326
SC_ICAero | 12.11% | 1.198% | I_GO_CC_J_1x1_DF | 91.7396 | 0.16 | 4.86 | 9211
SC_ICE | 9.183% | 0.1435% | I_GO_CC_J_2x1 | 62.916 | 1.95 | 14.45 | 6317
WD | 0% | 3.061% | I_GO_CC_J_2x1_DF | 91.2117 | 0.16 | 4.05 | 9158
WD_T | 0% | 3.061% | I_GO_SC_Aero | 91.5205 | 8.85 | 31.86 | 9189
|  |  | I_GO_SC_Frame | 95.7534 | 6.61 | 15.97 | 9614
|  |  | I_GO_SC_ICAero | 89.9568 | 6.14 | 22.82 | 9032
|  |  | I_GO_SC_ICE | 82.5268 | 7.45 | 29.82 | 8286
|  |  | I_GO_WD | 0 | 0 | 36.45 | n/a
|  |  | I_Hem_WD | 0 | 0 | 36.45 | n/a
|  |  | I_HTN_CC_GH_1x1 | 9.7071 | 2.12 | 24.74 | 6374
|  |  | I_HTN_CC_GH_1x1_DF | 13.9683 | 0.15 | 5.39 | 9172
|  |  | I_HTN_CC_GH_2x1 | 9.6934 | 2.01 | 16.63 | 6365
|  |  | I_HTN_CC_GH_2x1_DF | 13.9211 | 0.16 | 4.44 | 9141
|  |  | I_HTN_CC_J_1x1 | 9.634 | 2.05 | 21.26 | 6326
|  |  | I_HTN_CC_J_1x1_DF | 14.0277 | 0.16 | 4.86 | 9211
|  |  | I_HTN_CC_J_2x1 | 9.6203 | 1.95 | 14.45 | 6317
|  |  | I_HTN_CC_J_2x1_DF | 13.947 | 0.16 | 4.05 | 9158
|  |  | I_HTN_SC_Aero | 13.9942 | 8.85 | 31.86 | 9189
|  |  | I_HTN_SC_Frame | 14.6414 | 6.61 | 15.97 | 9614
|  |  | I_HTN_SC_ICAero | 13.7551 | 6.14 | 22.82 | 9032
|  |  | I_HTN_SC_ICE | 12.619 | 7.45 | 29.82 | 8286
|  |  | I_HTR_CC_GH_1x1 | 9.7071 | 2.12 | 24.74 | 6374
|  |  | I_HTR_CC_GH_1x1_DF | 13.9683 | 0.15 | 5.39 | 9172
|  |  | I_HTR_CC_GH_2x1 | 9.6934 | 2.01 | 16.63 | 6365
|  |  | I_HTR_CC_GH_2x1_DF | 13.9211 | 0.16 | 4.44 | 9141
|  |  | I_HTR_CC_J_1x1 | 9.634 | 2.05 | 21.26 | 6326
|  |  | I_HTR_CC_J_1x1_DF | 14.0277 | 0.16 | 4.86 | 9211
|  |  | I_HTR_CC_J_2x1 | 9.6203 | 1.95 | 14.45 | 6317
|  |  | I_HTR_CC_J_2x1_DF | 13.947 | 0.16 | 4.05 | 9158
|  |  | I_HTR_SC_Aero | 13.9942 | 8.85 | 31.86 | 9189
|  |  | I_HTR_SC_Frame | 14.6414 | 6.61 | 15.97 | 9614
|  |  | I_HTR_SC_ICAero | 13.7551 | 6.14 | 22.82 | 9032
|  |  | I_HTR_SC_ICE | 12.619 | 7.45 | 29.82 | 8286
|  |  | I_JB_CC_GH_1x1 | 6.3373 | 2.25 | 26.2 | 6395
|  |  | I_JB_CC_GH_1x1_DF | 9.4381 | 0.15 | 5.39 | 9524
|  |  | I_JB_CC_GH_2x1 | 6.3274 | 2.13 | 17.61 | 6385
|  |  | I_JB_CC_GH_2x1_DF | 9.3757 | 0.16 | 4.44 | 9461
|  |  | I_JB_CC_J_1x1 | 6.2789 | 2.15 | 22.33 | 6336
|  |  | I_JB_CC_J_1x1_DF | 9.4381 | 0.16 | 4.86 | 9524
|  |  | I_JB_CC_J_2x1 | 6.2699 | 2.05 | 15.18 | 6327
|  |  | I_JB_CC_J_2x1_DF | 9.3836 | 0.16 | 4.06 | 9469
|  |  | I_JB_SC_Aero | 9.1121 | 9.6 | 34.56 | 9195
|  |  | I_JB_SC_Frame | 9.5184 | 6.96 | 16.81 | 9605
|  |  | I_JB_SC_ICAero | 8.9218 | 6.45 | 24 | 9003
|  |  | I_JB_SC_ICE | 8.3015 | 7.75 | 31.04 | 8377
|  |  | I_NTN_CC_J_1x1 | 9.6493 | 2.15 | 22.33 | 6336
|  |  | I_NTN_CC_J_1x1_DF | 14.5043 | 0.16 | 4.86 | 9524
|  |  | I_NTN_CC_J_2x1 | 9.6356 | 2.05 | 15.18 | 6327
|  |  | I_NTN_CC_J_2x1_DF | 14.4206 | 0.16 | 4.06 | 9469
|  |  | I_NTN_SC_Aero | 14.0033 | 9.6 | 34.56 | 9195
|  |  | I_NTN_SC_Frame | 14.6277 | 6.96 | 16.81 | 9605
|  |  | I_NTN_SC_ICAero | 13.7109 | 6.45 | 24 | 9003
|  |  | I_NTN_SC_ICE | 12.7576 | 7.75 | 31.04 | 8377
|  |  | I_PNC_BAT_FL | 0 | 0 | 0 | 0
|  |  | I_PNC_BAT_LI | 0 | 0 | 0 | 0
|  |  | I_PNC_CC_GH_1x1 | 22.792 | 1.76 | 20.52 | 6363
|  |  | I_PNC_CC_GH_1x1_DF | 31.7541 | 0.15 | 5.39 | 8865
|  |  | I_PNC_CC_GH_2x1 | 22.7526 | 1.67 | 13.79 | 6352
|  |  | I_PNC_CC_GH_2x1_DF | 31.5643 | 0.16 | 4.44 | 8812
|  |  | I_PNC_CC_J_1x1 | 22.6273 | 1.7 | 17.66 | 6317
|  |  | I_PNC_CC_J_1x1_DF | 31.8007 | 0.16 | 4.86 | 8878
|  |  | I_PNC_CC_J_2x1 | 22.595 | 1.62 | 12 | 6308
|  |  | I_PNC_CC_J_2x1_DF | 31.6287 | 0.16 | 4.05 | 8830
|  |  | I_PNC_SC_Aero | 32.9684 | 7.54 | 27.14 | 9204
|  |  | I_PNC_SC_Frame | 34.4012 | 5.5 | 13.28 | 9604
|  |  | I_PNC_SC_ICAero | 32.1696 | 5.05 | 18.78 | 8981
|  |  | I_PNC_SC_ICE | 29.6551 | 7.45 | 29.82 | 8279
|  |  | I_SO_BAT_FL | 0 | 0 | 0 | 0
|  |  | I_SO_BAT_LI | 0 | 0 | 0 | 0
|  |  | I_SO_CC_GH_1x1 | 11.6794 | 1.97 | 22.92 | 6366
|  |  | I_SO_CC_GH_1x1_DF | 16.6128 | 0.15 | 5.39 | 9055
|  |  | I_SO_CC_GH_2x1 | 11.6538 | 1.86 | 15.39 | 6352
|  |  | I_SO_CC_GH_2x1_DF | 16.534 | 0.16 | 4.44 | 9012
|  |  | I_SO_CC_J_1x1 | 11.5969 | 1.9 | 19.73 | 6321
|  |  | I_SO_CC_J_1x1_DF | 16.6716 | 0.16 | 4.86 | 9087
|  |  | I_SO_CC_J_2x1 | 11.573 | 1.81 | 13.41 | 6308
|  |  | I_SO_CC_J_2x1_DF | 16.5835 | 0.16 | 4.05 | 9039
|  |  | I_SO_GEO_PPA | 0 | 77.34 | 0 | n/a
|  |  | I_SO_PUMP | 0 | 0 | 21.1 | 0
|  |  | I_SO_PV50FT | 0 | 0 | 18.47 | n/a
|  |  | I_SO_PV50FTI | 0 | 0 | 18.47 | n/a
|  |  | I_SO_PV50ST | 0 | 0 | 19.44 | n/a
|  |  | I_SO_PV50ST1 | 0 | 0 | 19.44 | n/a
|  |  | I_SO_SC_Aero | 16.8477 | 8.21 | 29.58 | 9183
|  |  | I_SO_SC_Frame | 17.6329 | 6.13 | 14.81 | 9611
|  |  | I_SO_SC_ICAero | 16.5413 | 5.67 | 21.1 | 9016
|  |  | I_SO_SC_ICE | 15.1891 | 7.45 | 29.82 | 8279
|  |  | I_SO_WD_T | 0 | 0 | 36.45 | n/a
|  |  | I_UN_BAT_FL | 0 | 0 | 0 | 0
|  |  | I_UN_BAT_LI | 0 | 0 | 0 | 0
|  |  | I_UN_CC_GH_1x1 | 9.7071 | 2.12 | 24.74 | 6374
|  |  | I_UN_CC_GH_1x1_DF | 13.9683 | 0.15 | 5.39 | 9172
|  |  | I_UN_CC_GH_2x1 | 9.6934 | 2.01 | 16.63 | 6365
|  |  | I_UN_CC_GH_2x1_DF | 13.9211 | 0.16 | 4.44 | 9141
|  |  | I_UN_CC_J_1x1 | 9.634 | 2.05 | 21.26 | 6326
|  |  | I_UN_CC_J_1x1_DF | 14.0277 | 0.16 | 4.86 | 9211
|  |  | I_UN_CC_J_2x1 | 9.6203 | 1.95 | 14.45 | 6317
|  |  | I_UN_CC_J_2x1_DF | 13.947 | 0.16 | 4.05 | 9158
|  |  | I_UN_NUC_AD | 0 | 11.37 | 98.35 | 0
|  |  | I_UN_NUC_MD | 0 | 15 | 167.77 | 0
|  |  | I_UN_SC_Aero | 13.9942 | 8.85 | 31.86 | 9189
|  |  | I_UN_SC_Frame | 14.6414 | 6.61 | 15.97 | 9614
|  |  | I_UN_SC_ICAero | 13.7551 | 6.14 | 22.82 | 9032
|  |  | I_UN_SC_ICE | 12.619 | 7.45 | 29.82 | 8286
|  |  | I_US_BAT_FL | 0 | 0 | 0 | 0
|  |  | I_US_BAT_LI | 0 | 0 | 0 | 0
|  |  | I_US_CAES | 0 | 0.77 | 18.9 | 4227
|  |  | I_US_CC_GH_1x1 | 9.7071 | 2.12 | 24.74 | 6374
|  |  | I_US_CC_GH_1x1_DF | 13.9683 | 0.15 | 5.39 | 9172
|  |  | I_US_CC_GH_2x1 | 9.6934 | 2.01 | 16.63 | 6365
|  |  | I_US_CC_GH_2x1_DF | 13.9211 | 0.16 | 4.44 | 9141
|  |  | I_US_CC_J_1x1 | 9.634 | 2.05 | 21.26 | 6326
|  |  | I_US_CC_J_1x1_DF | 14.0277 | 0.16 | 4.86 | 9211
|  |  | I_US_CC_J_2x1 | 9.6203 | 1.95 | 14.45 | 6317
|  |  | I_US_CC_J_2x1_DF | 13.947 | 0.16 | 4.05 | 9158
|  |  | I_US_GEO_B35 | 0 | 1.12 | 100.51 | n/a
|  |  | I_US_GEO_PPA | 0 | 77.34 | 0 | n/a
|  |  | I_US_PV50FT | 0 | 0 | 18.45 | n/a
|  |  | I_US_PV50FTI | 0 | 0 | 18.45 | n/a
|  |  | I_US_PV50ST | 0 | 0 | 19.41 | n/a
|  |  | I_US_PV50ST1 | 0 | 0 | 19.41 | n/a
|  |  | I_US_SC_Aero | 13.9942 | 8.85 | 31.86 | 9189
|  |  | I_US_SC_Frame | 14.6414 | 6.61 | 15.97 | 9614
|  |  | I_US_SC_ICAero | 13.7551 | 6.14 | 22.82 | 9032
|  |  | I_US_SC_ICE | 12.619 | 7.45 | 29.82 | 8286
|  |  | I_US_WD | 0 | 0 | 36.45 | n/a
|  |  | I_WAE_WD | 0 | 0.65 | 36.45 | n/a
|  |  | I_WNE_BAT_FL | 0 | 0 | 0 | 0
|  |  | I_WNE_BAT_LI | 0 | 0 | 0 | 0
|  |  | I_WNE_CC_GH_1x1 | 36.9195 | 2.12 | 24.74 | 6374
|  |  | I_WNE_CC_GH_1x1_DF | 53.126 | 0.15 | 5.39 | 9172
|  |  | I_WNE_CC_GH_2x1 | 36.8673 | 2.01 | 16.63 | 6365
|  |  | I_WNE_CC_GH_2x1_DF | 52.9465 | 0.16 | 4.44 | 9141
|  |  | I_WNE_CC_J_1x1 | 36.6414 | 2.05 | 21.26 | 6326
|  |  | I_WNE_CC_J_1x1_DF | 53.3519 | 0.16 | 4.86 | 9211
|  |  | I_WNE_CC_J_2x1 | 36.5893 | 1.95 | 14.45 | 6317
|  |  | I_WNE_CC_J_2x1_DF | 53.045 | 0.16 | 4.05 | 9158
|  |  | I_WNE_SC_Aero | 53.2245 | 8.85 | 31.86 | 9189
|  |  | I_WNE_SC_Frame | 55.6862 | 6.61 | 15.97 | 9614
|  |  | I_WNE_SC_ICAero | 52.3151 | 6.14 | 22.82 | 9032
|  |  | I_WNE_SC_ICE | 47.9942 | 7.45 | 29.82 | 8286
|  |  | I_WSW_BAT_FL | 0 | 0 | 0 | 0
|  |  | I_WSW_BAT_LI | 0 | 0 | 0 | 0
|  |  | I_WSW_CAES | 0 | 0.77 | 18.9 | 0
|  |  | I_WSW_CC_GH_1x1 | 6.3373 | 2.25 | 26.2 | 6395
|  |  | I_WSW_CC_GH_1x1_DF | 9.4381 | 0.15 | 5.39 | 9524
|  |  | I_WSW_CC_GH_2x1 | 6.3274 | 2.13 | 17.61 | 6385
|  |  | I_WSW_CC_GH_2x1_DF | 9.3757 | 0.16 | 4.44 | 9461
|  |  | I_WSW_CC_J_1x1 | 6.2789 | 2.15 | 22.33 | 6336
|  |  | I_WSW_CC_J_1x1_DF | 9.4381 | 0.16 | 4.86 | 9524
|  |  | I_WSW_CC_J_2x1 | 6.2699 | 2.05 | 15.18 | 6327
|  |  | I_WSW_CC_J_2x1_DF | 9.3836 | 0.16 | 4.06 | 9469
|  |  | I_WSW_NUC_AD | 0 | 11.37 | 98.35 | 0
|  |  | I_WSW_NUC_MD | 0 | 15 | 167.77 | 0
|  |  | I_WSW_PUMP | 0 | 0 | 15.58 | 0
|  |  | I_WSW_SC_Aero | 9.1121 | 9.6 | 34.56 | 9195
|  |  | I_WSW_SC_Frame | 9.5184 | 6.96 | 16.81 | 9605
|  |  | I_WSW_SC_ICAero | 8.9218 | 6.45 | 24 | 9003
|  |  | I_WSW_SC_ICE | 8.3015 | 7.75 | 31.04 | 8377
|  |  | I_WV_BAT_FL | 0 | 0 | 0 | 0
|  |  | I_WV_BAT_LI | 0 | 0 | 0 | 0
|  |  | I_WV_CC_GH_1x1 | 22.7885 | 1.86 | 21.68 | 6362
|  |  | I_WV_CC_GH_1x1_DF | 32.2807 | 0.15 | 5.39 | 9012
|  |  | I_WV_CC_GH_2x1 | 22.7562 | 1.77 | 14.57 | 6353
|  |  | I_WV_CC_GH_2x1_DF | 32.1266 | 0.16 | 4.44 | 8969
|  |  | I_WV_CC_J_1x1 | 22.6273 | 1.8 | 18.67 | 6317
|  |  | I_WV_CC_J_1x1_DF | 32.363 | 0.16 | 4.86 | 9035
|  |  | I_WV_CC_J_2x1 | 22.5807 | 1.71 | 12.69 | 6304
|  |  | I_WV_CC_J_2x1_DF | 31.901 | 0.16 | 4.05 | 8906
|  |  | I_WV_SC_Aero | 32.843 | 7.76 | 27.96 | 9169
|  |  | I_WV_SC_Frame | 34.4012 | 5.81 | 14.02 | 9604
|  |  | I_WV_SC_ICAero | 32.2377 | 5.35 | 19.88 | 9000
|  |  | I_WV_SC_ICE | 29.6551 | 7.45 | 29.82 | 8279
|  |  | I_WW_BAT_Fl | 0 | 0 | 0 | 0
|  |  | I_WW_BAT_LI | 0 | 0 | 0 | 0
|  |  | I_WW_CC_GH_1x1 | 22.7885 | 1.86 | 21.68 | 6362
|  |  | I_WW_CC_GH_1x1_DF | 32.2807 | 0.15 | 5.39 | 9012
|  |  | I_WW_CC_GH_2x1 | 22.7562 | 1.77 | 14.57 | 6353
|  |  | I_WW_CC_GH_2x1_DF | 32.1266 | 0.16 | 4.44 | 8969
|  |  | I_WW_CC_J_1x1 | 22.6273 | 1.8 | 18.67 | 6317
|  |  | I_WW_CC_J_1x1_DF | 32.363 | 0.16 | 4.86 | 9035
|  |  | I_WW_CC_J_2x1 | 22.5807 | 1.71 | 12.69 | 6304
|  |  | I_WW_CC_J_2x1_DF | 31.901 | 0.16 | 4.05 | 8906
|  |  | I_WW_NUC_MD | 0 | 15 | 167.77 | 0
|  |  | I_WW_PUMP | 0 | 0 | 16.86 | 0
|  |  | I_WW_SC_Aero | 32.843 | 7.76 | 27.96 | 9169
|  |  | I_WW_SC_Frame | 34.4012 | 5.81 | 14.02 | 9604
|  |  | I_WW_SC_ICAero | 32.2377 | 5.35 | 19.88 | 9000
|  |  | I_WW_SC_ICE | 29.6551 | 7.45 | 29.82 | 8279
|  |  | I_WW_WD | 0 | 0 | 36.45 | n/a
|  |  | I_WYD_SC_Aero | 53.2593 | 9.6 | 34.56 | 9195
|  |  | I_WYD_SC_Frame | 55.6341 | 6.96 | 16.81 | 9605
|  |  | I_WYD_SC_ICAero | 52.1472 | 6.45 | 24 | 9003
|  |  | I_WYD_SC_ICE | 48.5212 | 7.75 | 31.04 | 8377
|  |  | I_YK_BAT_FL | 0 | 0 | 0 | 0
|  |  | I_YK_BAT_LI | 0 | 0 | 0 | 0
|  |  | I_YK_CC_GH_1x1 | 22.792 | 1.76 | 20.52 | 6363
|  |  | I_YK_CC_GH_1x1_DF | 31.7541 | 0.15 | 5.39 | 8865
|  |  | I_YK_NUC_MD | 0 | 15 | 167.77 | 0
|  |  | I_YK_PV50FT | 0 | 0 | 18.47 | n/a
|  |  | I_YK_PV50FTI | 0 | 0 | 18.47 | n/a
|  |  | I_YK_PV50ST | 0 | 0 | 19.44 | n/a
|  |  | I_YK_PV50ST1 | 0 | 0 | 19.44 | n/a
|  |  | I_YK_SC_Frame | 34.4012 | 5.5 | 13.28 | 9604
|  |  | I_YK_SC_ICAero | 32.1696 | 5.05 | 18.78 | 8981
|  |  | I_YK_WD | 0 | 0 | 36.45 | n/a

## Reference
Resource I | Resource II | Location I | Location II
SC_Aero | Single Cycle Combustion Turbine (SCCT) Aero | Dave Johnston | I_DJ_
SC_ICAero | Intercooled SCCT Aero | Goshen | I_GO_
SC_Frame | Single Cycle Combustion Turbine (SCCT) Frame | Hunter | I_HTR_
SC_ICE | Internal Combustion Engines | Huntington | I_HTN_
CC_GH_1x1 | Combined Cycle Combustion Turbine (CCCT) | Jim Bridger | I_JB_
CC_GH_1x1_DF | Combined Cycle Combustion Turbine (CCCT) | Naughton | I_NTN_
CC_GH_2x1 | Combined Cycle Combustion Turbine (CCCT) | Pacific Northwest | I_PNC_
CC_GH_2x1_DF | Combined Cycle Combustion Turbine (CCCT) | Southern Oregon - California | I_SO_
CC_J_1x1 | Combined Cycle Combustion Turbine (CCCT) | Utah North | I_UN_
CC_J_1x1_DF | Combined Cycle Combustion Turbine (CCCT) | Utah South | I_US_
CC_J_2x1 | Combined Cycle Combustion Turbine (CCCT) | Walla Walla | I_WW_
CC_J_2x1_DF | Combined Cycle Combustion Turbine (CCCT) | WY-NE | I_WYNE_
GEO_B35 | Geothermal | Wyodak | I_WYD_
GEO_PPA | Geothermal | Wyoming-AE | I_WAE_
WD | Wind | WY-SW | I_WSW_
WD_T | Wind | Yakima | I_YK_
PV50FT | Solar - Rooftop Photovoltaic
PV50ST | Solar - Rooftop Photovoltaic
PUMP | Pumped Storage
CAES | Compressed Air Energy Storage (CAES)
NUC_AD | Nuclear Production Plant
NUC_MD | Nuclear Production Plant
Biomass
Concentrating Solar Power Tower
Concentrating Solar Power Tower (Thermal Storage)
Concentrating Solar Power with Natural Gas (Thermal Storage)