## 2019 IRP Chapter 6
Transmission Integration Cost by Location and Capacity Increment
IRP Bubble | Added Resource MW |  | IRP Year | Description of Integration | Affected Topology Path(s)
| Min | Max |  |  | Incremental Capacity (if any) | From Bubble | To Bubble
Portland/N. Coast | 1 | 130 | 2024 | Portland area local reinforcement | - | - | -
| 131 | 580 | 2030 | Portland area (Troutdale) to Albany area 230 kV transmission | 450 | Portland | Willamette
Willamette | 1 | 615 | 2024 | Albany area local reinforcement | - | - | -
| 616 | 1115 | 2030 | Albany area to Roseburg area 500 kV transmission | 1500 | Willamette | South-Central Oregon
Yakima | 1 | 405 | 2024 | Yakima area local reinforcement | - | - | -
| 406 | 835 | 2030 | Yakima area to Bend area 230 kV transmission | 450 | Yakima | South-Central Oregon
Walla Walla | 1 | 100 | 2030 | Walla Walla area to Yakima lower valley transmission | 200 | Walla Walla | Yakima
South-Central OR/N. California | 1 | 500 | 2024 | Medford area 500-230 kV and 230 kV reinforcement | - | - | -
| 501 | 975 | 2025 | Medford area 500-230 kV and 230 kV reinforcement | - | - | -
Bridger | 1 | 650 | 2026 | Energy Gateway segment D.2 (Anticline-Populus 500 kV transmission line) | 650 | Bridger | Bridger West (Populus)
Goshen | 1 | 450 | 2023 | Southern Idaho reinforcement | - | - | -
| 451 | 1100 | 2029 | Southern Idaho reinforcement | 800 | Goshen | Utah North
Wyoming NE | 1 | 460 | 2023 | Energy Gateway segment D.1 (Windstar - Shirley Basin 230 kV line) | - | - | -
Wyoming SW | 1 | 100 | 2024 | Southwest Wyoming area reinforcement | - | - | -
| 101 | 500 | 2026 | Separation of double circuit 230 kV lines, Southwest Wyoming/northern Utah area | - | - | -
Aeolus | 1 | 1920 | 2024 | Energy Gateway segment F (Aeolus-Clover 500 kV transmission line) | 1700 | Aeolus | Utah South
Utah North | 1 | 300 | 2021 | Northern Utah 345 kV reinforcement | - | - | -
| 301 | 900 | 2024 | Northern Utah 345 kV reinforcement | - | Utah North | Utah North
Utah South | 1 | 300 | 2021 | Utah Valley area 345-138 kV and 138 kV local reinforcement | - | - | -
| 301 | 800 | 2027 | Utah Valley area local 138 kV reinforcement | - | - | -
NOTES
Note: The scope and cost of transmission upgrades are planning estimates. Actual scope and costs will vary depending upon the interconnection queue, the transmission service queue, the specific location of any given project and the type of equipment proposed for any given project.