## Table of Contents
Table List
Tables 7.2-7.5 (Ch 7)
DB-No Deltas - combined

## Table List
Table 7.1 - Supply-Side Resource Option Tables
| Characteristics and Costs | Operating Characteristics and Environmental Data
Thermal | Table 7.2 | Table 7.4
Non-Thermal and Storage | Table 7.3 | Table 7.5
| Additional Attributes and Fixed O&M | Variable O&M, Total Cost and Credits
Thermal | Table 7.6 | Table 7.9
Non-Thermal | Table 7.7 | Table 7.10
Storage | Table 7.8 | Table 7.11

## Tables 7.2-7.5 (Ch 7)
Table 7.2 – 2025 Thermal Supply-Side Resources, Characteristics and Costs (2024$) | [14 empty] | Table 7.4 – 2025 Thermal Supply-Side Resources, Operating Characteristics and Environmental Data(2024$)
Fuel | Resource Description | Characteristics | [5 empty] | Costs | [6 empty] | Fuel | Resource Description | Operating Characteristics |  |  |  | Environmental Data
|  | Elevation (AFSL) | Net Capacity (MW) | Resource Availability Year | Total Implementation Time (yrs) | Commercial Operation Year | Asset Life (yrs) | Base Capital ($/kW) | Var O&M ($/MWh) | Fraction Var O&M Capitalized | Fraction Var O&M Adjusted by Capacity Changes | Fixed O&M ($/kW-yr) | Fraction Fixed O&M Capitalized | Demolition Cost ($/kW) |  |  | Average Full Load Heat Rate (HHV Btu/KWh) | Efficiency | EFOR (%) | POR (%) | Water Consumed (Gal/MWh) | SO2 (lbs/MMBtu) | NOx (lbs/MMBtu) | Hg (lbs/TBTu) | CO2 (lbs/MMBtu)
Biofuel | Internal Combustion Engine, renewable biofuel, with SCR & 24-hour fuel tank | 0 | 20 | 2025 | 2.5 | 2027 | 30 | 2130.9413 | 6.9294 | 74% | 91% | 42.8183 | 3% | 14.5945 | Biofuel | Internal Combustion Engine, renewable biofuel, with SCR & 24-hour fuel tank | 8295 | 41.13% | 2.5% | 5% | 27.1 | 0.001515 | 0.02 | 0 | 117
Natural Gas | SCCT Aero, with SCR | 0 | 50 | 2025 | 3.5 | 2028 | 40 | 2612.7968 | 7.4029 | 87% | 98% | 12.4161 | 3% | 32.459 | Natural Gas | SCCT Aero, with SCR | 9447 | 36.12% | 2.9% | 3.9% | 27 | 0.001504 | 0.0075 | 0 | 117
Natural Gas | SCCT Aero x4, with SCR | 0 | 211 | 2025 | 3.5 | 2028 | 40 | 1789.352 | 5.9223 | 87% | 98% | 9.9328 | 3% | 32.459 | Natural Gas | SCCT Aero x4, with SCR | 9447 | 36.12% | 2.9% | 3.9% | 27 | 0.001504 | 0.0075 | 0 | 117
Natural Gas | SCCT Frame "F" x1, with SCR | 0 | 233 | 2025 | 5 | 2030 | 40 | 1386.9222 | 7.7513 | 100% | 99% | 27.9225 | 3% | 12.13 | Natural Gas | SCCT Frame "F" x1, with SCR | 9717 | 35.12% | 2.7% | 3.9% | 28.4 | 0.001504 | 0.0075 | 0 | 117
Natural Gas | CCCT Dry "H", 1X1, DF, with SCR | 0 | 649 | 2025 | 5 | 2030 | 40 | 1838.9982 | 2.7029 | 0% | 100% | 42.4422 | 0% | 12.082 | Natural Gas | CCCT Dry "H", 1X1, DF, with SCR | 6040 | 56.49% | 2.5% | 3.8% | 210 | 0.001504 | 0.0075 | 0 | 117
Natural Gas | CCCT Dry "H", 2X1, DF, with SCR | 0 | 1227 | 2025 | 5 | 2030 | 40 | 1553.2592 | 2.2785 | 0% | 100% | 35.1823 | 0% | 11.886 | Natural Gas | CCCT Dry "H", 2X1, DF, with SCR | 6122 | 55.74% | 2.5% | 3.8% | 210 | 0.001504 | 0.0075 | 0 | 117
Natural Gas | CCCT Dry "H", 1X1, DF, with SCR + Δ for adding 95% CCS to new CCCT 1x1 | 0 | 565.4765 | 2025 | 5 | 2030 | 40 | 3429.3765 | 5.3164 | 0% | 100% | 77.0661 | 0% | 65.2793 | Natural Gas | CCCT Dry "H", 1X1, DF, with SCR + Δ for adding 95% CCS to new CCCT 1x1 | 6743 | 53.17% | 2.5% | 3.8% | 323.4 | 0.001504 | 0.005625 | 0 | 5.8204
Natural Gas | CCCT Dry "H", 2X1, DF, with SCR + Δ for adding 95% CCS to new CCCT 2x1 | 0 | 1084.7571 | 2025 | 5 | 2030 | 40 | 2846.0201 | 4.825 | 0% | 100% | 62.9932 | 0% | 65.0833 | Natural Gas | CCCT Dry "H", 2X1, DF, with SCR + Δ for adding 95% CCS to new CCCT 2x1 | 6843 | 52.46% | 2.5% | 3.8% | 323.4 | 0.001504 | 0.005625 | 0 | 5.8204
Natural Gas | Internal Combustion Engine, renewable biofuel, with SCR & 24-hour fuel tank + Δ for CT Brownfield construction | 0 | 20 | 2025 | 2.5 | 2027 | 30 | 1917.8471 | 6.2364 | 74% | 91% | 42.8183 | 3% | 14.5945 | Natural Gas | Internal Combustion Engine, renewable biofuel, with SCR & 24-hour fuel tank + Δ for CT Brownfield construction | 8295 | 41.13% | 2.5% | 5% | 27.1 | 0.001515 | 0.02131 | 0 | 117
Natural Gas | SCCT Aero, with SCR + Δ for CT Brownfield construction | 0 | 50 | 2025 | 3.5 | 2028 | 40 | 2351.5171 | 6.6626 | 87% | 98% | 12.4161 | 3% | 32.459 | Natural Gas | SCCT Aero, with SCR + Δ for CT Brownfield construction | 9447 | 36.12% | 2.9% | 3.9% | 27 | 0.001504 | 0.0079913 | 0 | 117
Natural Gas | SCCT Aero x4, with SCR + Δ for CT Brownfield construction | 0 | 211 | 2025 | 3.5 | 2028 | 40 | 1610.4168 | 5.3301 | 87% | 98% | 9.9328 | 3% | 32.459 | Natural Gas | SCCT Aero x4, with SCR + Δ for CT Brownfield construction | 9447 | 36.12% | 2.9% | 3.9% | 27 | 0.001504 | 0.0079913 | 0 | 117
Natural Gas | SCCT Frame "F" x1, with SCR + Δ for CT Brownfield construction | 0 | 233 | 2025 | 5 | 2030 | 40 | 1248.23 | 6.9762 | 100% | 99% | 27.9225 | 3% | 12.13 | Natural Gas | SCCT Frame "F" x1, with SCR + Δ for CT Brownfield construction | 9717 | 35.12% | 2.7% | 3.9% | 28.4 | 0.001504 | 0.0079913 | 0 | 117
Natural Gas | CCCT Dry "H", 1X1, DF, with SCR + Δ for CT Brownfield construction | 0 | 649 | 2025 | 5 | 2030 | 40 | 1655.0984 | 2.4326 | 0% | 100% | 42.4422 | 0% | 12.082 | Natural Gas | CCCT Dry "H", 1X1, DF, with SCR + Δ for CT Brownfield construction | 6040 | 56.49% | 2.5% | 3.8% | 210 | 0.001504 | 0.0079913 | 0 | 117
Natural Gas | CCCT Dry "H", 2X1, DF, with SCR + Δ for CT Brownfield construction | 0 | 1227 | 2025 | 5 | 2030 | 40 | 1397.9333 | 2.0506 | 0% | 100% | 35.1823 | 0% | 11.886 | Natural Gas | CCCT Dry "H", 2X1, DF, with SCR + Δ for CT Brownfield construction | 6122 | 55.74% | 2.5% | 3.8% | 210 | 0.001504 | 0.0079913 | 0 | 117
Natural Gas | CCCT Dry "H", 1X1, DF, with SCR + Δ for adding 95% CCS to new CCCT 1x1 + Δ for CT Brownfield construction | 0 | 565.4765 | 2025 | 5 | 2030 | 40 | 3086.4388 | 4.7848 | 0% | 100% | 77.0661 | 0% | 65.2793 | Natural Gas | CCCT Dry "H", 1X1, DF, with SCR + Δ for adding 95% CCS to new CCCT 1x1 + Δ for CT Brownfield construction | 6743 | 53.17% | 2.5% | 3.8% | 323.4 | 0.001504 | 0.0059934 | 0 | 5.8204
Natural Gas | CCCT Dry "H", 2X1, DF, with SCR + Δ for adding 95% CCS to new CCCT 2x1 + Δ for CT Brownfield construction | 0 | 1084.7571 | 2025 | 5 | 2030 | 40 | 2561.4181 | 4.3425 | 0% | 100% | 62.9932 | 0% | 65.0833 | Natural Gas | CCCT Dry "H", 2X1, DF, with SCR + Δ for adding 95% CCS to new CCCT 2x1 + Δ for CT Brownfield construction | 6843 | 52.46% | 2.5% | 3.8% | 323.4 | 0.001504 | 0.0059934 | 0 | 5.8204
Hydrogen | SCCT Frame "F" x1, with SCR + Δ for 100%Hydrogen burning capability | 0 | 233 | 2025 | 5 | 2030 | 40 | 1594.9605 | 8.914 | 100% | 99% | 27.9225 | 3% | 13.9495 | Hydrogen | SCCT Frame "F" x1, with SCR + Δ for 100%Hydrogen burning capability | 9717 | 35.12% | 2.7% | 3.9% | 28.4 | 0 | 0.0075 | 0 | 0
Hydrogen | CCCT Dry "H", 1X1, DF, with SCR + Δ for 100%Hydrogen burning capability | 0 | 649 | 2025 | 5 | 2030 | 40 | 2114.8479 | 3.1083 | 0% | 100% | 42.4422 | 0% | 13.8942 | Hydrogen | CCCT Dry "H", 1X1, DF, with SCR + Δ for 100%Hydrogen burning capability | 6040 | 56.49% | 2.5% | 3.8% | 210 | 0 | 0.0075 | 0 | 0
Hydrogen | CCCT Dry "H", 2X1, DF, with SCR + Δ for 100%Hydrogen burning capability | 0 | 1227 | 2025 | 5 | 2030 | 40 | 1786.2481 | 2.6202 | 0% | 100% | 35.1823 | 0% | 13.6689 | Hydrogen | CCCT Dry "H", 2X1, DF, with SCR + Δ for 100%Hydrogen burning capability | 6122 | 55.74% | 2.5% | 3.8% | 210 | 0 | 0.0075 | 0 | 0
Hydrogen | SCCT Frame "F" x1, with SCR + Δ for Hydrogen storage, cavern, 80 bar, 24 hour | 0 | 233 | 2025 | 5 | 2030 | 40 | 2585.9322 | 8.1775 | 100% | 99% | 35.1241 | 3% | 27.13 | Hydrogen | SCCT Frame "F" x1, with SCR + Δ for Hydrogen storage, cavern, 80 bar, 24 hour | 9717 | 35.12% | 2.754% | 3.9% | 28.4 | 0.001962 | 0.009462 | 0.001962 | 0.001962
Hydrogen | CCCT Dry "H", 1X1, DF, with SCR + Δ for Hydrogen storage, cavern, 80 bar, 24 hour | 0 | 649 | 2025 | 5 | 2030 | 40 | 3038.0082 | 3.1291 | 0% | 100% | 49.6438 | 0% | 27.082 | Hydrogen | CCCT Dry "H", 1X1, DF, with SCR + Δ for Hydrogen storage, cavern, 80 bar, 24 hour | 6040 | 56.49% | 2.55% | 3.8% | 210 | 0.001962 | 0.009462 | 0.001962 | 0.001962
Hydrogen | CCCT Dry "H", 2X1, DF, with SCR + Δ for Hydrogen storage, cavern, 80 bar, 24 hour | 0 | 1227 | 2025 | 5 | 2030 | 40 | 2752.2692 | 2.7047 | 0% | 100% | 42.3839 | 0% | 26.886 | Hydrogen | CCCT Dry "H", 2X1, DF, with SCR + Δ for Hydrogen storage, cavern, 80 bar, 24 hour | 6122 | 55.74% | 2.55% | 3.8% | 210 | 0.001962 | 0.009462 | 0.001962 | 0.001962
Hydrogen | SCCT Frame "F" x1, with SCR + Δ for Hydrogen storage, tanks, 500 bar, 24 hour | 0 | 233 | 2025 | 5 | 2030 | 40 | 2097.8385 | 8.3231 | 100% | 99% | 40.7792 | 3% | 27.13 | Hydrogen | SCCT Frame "F" x1, with SCR + Δ for Hydrogen storage, tanks, 500 bar, 24 hour | 9717 | 35.12% | 2.754% | 3.9% | 28.4 | 0.001962 | 0.009462 | 0.001962 | 0.001962
Hydrogen | CCCT Dry "H", 1X1, DF, with SCR + Δ for Hydrogen storage, tanks, 500 bar, 24 hour | 0 | 649 | 2025 | 5 | 2030 | 40 | 2549.9145 | 3.2747 | 0% | 100% | 55.2989 | 0% | 27.082 | Hydrogen | CCCT Dry "H", 1X1, DF, with SCR + Δ for Hydrogen storage, tanks, 500 bar, 24 hour | 6040 | 56.49% | 2.55% | 3.8% | 210 | 0.001962 | 0.009462 | 0.001962 | 0.001962
Hydrogen | CCCT Dry "H", 2X1, DF, with SCR + Δ for Hydrogen storage, tanks, 500 bar, 24 hour | 0 | 1227 | 2025 | 5 | 2030 | 40 | 2264.1755 | 2.8502 | 0% | 100% | 48.0391 | 0% | 26.886 | Hydrogen | CCCT Dry "H", 2X1, DF, with SCR + Δ for Hydrogen storage, tanks, 500 bar, 24 hour | 6122 | 55.74% | 2.55% | 3.8% | 210 | 0.001962 | 0.009462 | 0.001962 | 0.001962
Natural Gas | CCCT Dry "H", 1X1, DF, with SCR, Advanced Technology Case + Δ advanced technology case, CCCT 1x1 | 0 | 649 | 2025 | 5 | 2030 | 40 | 1831.6324 | 2.6806 | 0% | 100% | 41.3253 | 0% | 12.082 | Natural Gas | CCCT Dry "H", 1X1, DF, with SCR, Advanced Technology Case + Δ advanced technology case, CCCT 1x1 | 6040 | 56.49% | 2.5% | 3.8% | 210 | 0.001504 | 0.0075 | 0 | 117
Natural Gas | CCCT Dry "H", 2X1, DF, with SCR, Advanced Technology Case + Δ advanced technology case, CCCT 2x1 | 0 | 1227 | 2025 | 5 | 2030 | 40 | 1517.8449 | 2.2338 | 0% | 100% | 34.0654 | 0% | 11.886 | Natural Gas | CCCT Dry "H", 2X1, DF, with SCR, Advanced Technology Case + Δ advanced technology case, CCCT 2x1 | 6122 | 55.74% | 2.5% | 3.8% | 210 | 0.001504 | 0.0075 | 0 | 117
Natural Gas | CCCT Dry "H", 1X1, DF, with SCR, Advanced Technology Case + Δ advanced technology case, CCCT 1x1 with 95% CCS | 0 | 565.4765 | 2025 | 5 | 2030 | 40 | 3260.8848 | 5.0261 | 0% | 100% | 72.5985 | 0% | 65.2793 | Natural Gas | CCCT Dry "H", 1X1, DF, with SCR, Advanced Technology Case + Δ advanced technology case, CCCT 1x1 with 95% CCS | 6743 | 53.17% | 2.5% | 3.8% | 323.4 | 0.001504 | 0.005625 | 0 | 5.8204
Natural Gas | CCCT Dry "H", 2X1, DF, with SCR, Advanced Technology Case + Δ advanced technology case, CCCT 2x1 with 95% CCS | 0 | 1084.7571 | 2025 | 5 | 2030 | 40 | 2637.1218 | 4.4899 | 0% | 100% | 57.7437 | 0% | 65.0833 | Natural Gas | CCCT Dry "H", 2X1, DF, with SCR, Advanced Technology Case + Δ advanced technology case, CCCT 2x1 with 95% CCS | 6843 | 52.46% | 2.5% | 3.8% | 323.4 | 0.001504 | 0.005625 | 0 | 5.8204
Hydrogen | Electrolyzer, Proton Exchange Membrane (PEM), 50,000 kg/day | 0 | -118.625 | 2025 | 5 | 2030 | 40 | 560.9889 | 23.91 | 0% | 0 | 10.2819 | 100% | 32.459 | Hydrogen | Electrolyzer, Proton Exchange Membrane (PEM), 50,000 kg/day | N/A | 79.13% | 1.5% | 1.5% | 45.6621 | 0 | 0 | 0 | 0
Coal | CCS Dave Johnston 4 (costs on post retrofit basis) | 5541 | -84.61 | 2027 | 5 | 2032 | 30 | 3500.7808 | 11.3987 | 0% | 0% | 277.6774 | 0% | 53.1973 | Coal | CCS Dave Johnston 4 (costs on post retrofit basis) | 14794.5994 | 23.06% | 7.5% | 7.5% | 186 | 10 | 0.071 | 0.304 | 10
Coal | CCS Hunter 1-3 (costs on post retrofit basis) | 6429 | -296.9222 | 2027 | 5 | 2032 | 30 | 2951.2039 | 9.7288 | 0% | 0% | 235.3561 | 0% | 53.1973 | Coal | CCS Hunter 1-3 (costs on post retrofit basis) | 14011.4943 | 24.35% | 7.5% | 7.5% | 186 | 10 | 0.071 | 0.304 | 10
Coal | CCS Huntington 1&2 (costs on post retrofit basis) | 6933 | -233.0507 | 2027 | 5 | 2032 | 30 | 2951.3968 | 9.6326 | 0% | 0% | 242.12 | 0% | 53.1973 | Coal | CCS Huntington 1&2 (costs on post retrofit basis) | 13661.9109 | 24.98% | 7.5% | 7.5% | 186 | 10 | 0.071 | 0.304 | 10
Coal | CCS Jim Bridger 3&4 (costs on post retrofit basis) | 7513 | -174.3 | 2025 | 5 | 2030 | 30 | 2598.3838 | 10.5675 | 0% | 0% | 254.9074 | 0% | 53.1973 | Coal | CCS Jim Bridger 3&4 (costs on post retrofit basis) | 14483.2465 | 23.56% | 7.5% | 7.5% | 186 | 10 | 0.071 | 0.304 | 10
Coal | CCS Wyodak (costs on post retrofit basis) | 4448 | -68.7066 | 2027 | 5 | 2032 | 30 | 3504.2501 | 11.6873 | 0% | 0% | 309.506 | 0% | 53.1973 | Coal | CCS Wyodak (costs on post retrofit basis) | 16652.5135 | 20.49% | 7.5% | 7.5% | 186 | 10 | 0.071 | 0.304 | 10
Nuclear | Small Modular Reactor or Advanced Reactor, Moderate Technology Case | N/A | 600 | 2030 | 5 | 2035 | 60 | 9662.09 | 9.7419 | 0% | 0% | 97.4192 | 0% | 17 | Nuclear | Small Modular Reactor or Advanced Reactor, Moderate Technology Case | 9180 | 37.17% | 2% | 5% | 720 | 0 | 0 | 0 | 0
Nuclear | Small Modular Reactor or Advanced Reactor, Advanced Technology Case | N/A | 600 | 2030 | 4 | 2034 | 60 | 6368.2283 | 8.7391 | 0% | 0% | 84.5255 | 0% | 12 | Nuclear | Small Modular Reactor or Advanced Reactor, Advanced Technology Case | 9180 | 37.17% | 2% | 5% | 720 | 0 | 0 | 0 | 0
Nuclear | Small Modular Reactor or Advanced Reactor, Moderate Technology Case + Δ for nuclear integrated thermal storage | N/A | 750 | 2030 | 5 | 2035 | 60 | 10628.299 | 10.7161 | 0% | 0% | 107.1611 | 0% | 17 | Nuclear | Small Modular Reactor or Advanced Reactor, Moderate Technology Case + Δ for nuclear integrated thermal storage | 12626.4646 | 37.17% | 2% | 5% | 720 | 0 | 0 | 0 | 0
Nuclear | Small Modular Reactor or Advanced Reactor, Advanced Technology Case + Δ for nuclear integrated thermal storage | N/A | 750 | 2030 | 4 | 2034 | 60 | 7005.0511 | 9.613 | 0% | 0% | 92.978 | 0% | 12 | Nuclear | Small Modular Reactor or Advanced Reactor, Advanced Technology Case + Δ for nuclear integrated thermal storage | 12626.4646 | 37.17% | 2% | 5% | 720 | 0 | 0 | 0 | 0
Nuclear | Large Light Water Reactor, Moderate Technology Case | N/A | 2000 | 2030 | 7 | 2037 | 60 | 7562.8694 | 9.3838 | 0% | 0% | 125.3556 | 0% | 10 | Nuclear | Large Light Water Reactor, Moderate Technology Case | 10497 | 32.51% | 2% | 5% | 720 | 0 | 0 | 0 | 0
Nuclear | Large Light Water Reactor, Advanced Technology Case | N/A | 2000 | 2030 | 5 | 2035 | 60 | 6265.2501 | 7.8795 | 0% | 0% | 90.256 | 0% | 9 | Nuclear | Large Light Water Reactor, Advanced Technology Case | 10497 | 32.51% | 2% | 5% | 720 | 0 | 0 | 0 | 0
Geothermal | Near Field Enhanhanced Geothermal System (NF-EGS) Binary | N/A | 707 | 2025 | 3 | 2028 | 30 | 7593.0583 | included in FOM | 0% | 0% | 194 | 6.074% | 125.0883 | Geothermal | Near Field Enhanhanced Geothermal System (NF-EGS) Binary | N/A | N/A | 10% | 10% | 510 | n/a | n/a | n/a | n/a
Geothermal | Near Field Enhanhanced Geothermal System (NF-EGS) Binary + Δ Advanced Geothermal Technology Case | N/A | 707 | 2025 | 3 | 2028 | 30 | 5948.7894 | included in FOM | 0% | 0% | 173.9003 | 6.074% | 125.0883 | Geothermal | Near Field Enhanhanced Geothermal System (NF-EGS) Binary + Δ Advanced Geothermal Technology Case | N/A | N/A | 10% | 10% | 510 | n/a | n/a | n/a | n/a
Table 7.3 – 2025 Non-thermal Supply-Side Resources, Characteristics and Costs (2024$) | [14 empty] | Table 7.5 – 2025 Non-thermal Supply-Side Resources, Operating Characteristics and Environmental Data(2024$)
Fuel | Resource Description | Characteristics | [5 empty] | Costs | [6 empty] | Fuel | Resource Description | Operating Characteristics |  |  |  | Environmental Data
|  | Elevation (AFSL) | Net Capacity (MW) | Resource Availability Year | Total Implementation Time (yrs) | Commercial Operation Year | Asset Life (yrs) | Base Capital ($/kW) | Var O&M ($/MWh) | Fraction Var O&M Capitalized | Fraction Var O&M Adjusted by Capacity Changes | Fixed O&M ($/kW-yr) | Fraction Fixed O&M Capitalized | Demolition Cost ($/kW) |  |  | Average Full Load Heat Rate (HHV Btu/KWh) | Efficiency | EFOR (%) | POR (%) | Water Consumed (Gal/MWh) | SO2 (lbs/MMBtu) | NOx (lbs/MMBtu) | Hg (lbs/TBTu) | CO2 (lbs/MMBtu)
Storage1 | Li-Ion, 4-hour, 20 MW | N/A | 20 | 2025 | 1 | 2026 | 20 | 1747.6124 | Included in FOM | 0% | 0% | 45.0539 | 0% | 29.9368 | Storage1 | Li-Ion, 4-hour, 20 MW | n/a | 85% | 1% | included in CF | n/a | 0 | 0 | 0 | 0
Storage1 | Li-Ion, 4-hour, 200 MW | N/A | 200 | 2025 | 2 | 2027 | 20 | 1497.8945 | Included in FOM | 0% | 0% | 38.7667 | 0% | 25.6591 | Storage1 | Li-Ion, 4-hour, 200 MW | n/a | 85% | 1% | included in CF | n/a | 0 | 0 | 0 | 0
Storage1 | Li-Ion, 4-hour, 200 MW + Δ Double Duration, Li-Ion, 4-hour, 200MW | N/A | 200 | 2025 | 2 | 2027 | 20 | 2556.5743 | Included in FOM | 0% | 0% | 69.78 | 0% | 46.1865 | Storage1 | Li-Ion, 4-hour, 200 MW + Δ Double Duration, Li-Ion, 4-hour, 200MW | n/a | 85% | 1% | included in CF | n/a | 0 | 0 | 0 | 0
Storage1 | Li-Ion, 4-hour, 1000 MW | N/A | 1000 | 2025 | 3 | 2028 | 20 | 1459.4997 | Included in FOM | 0% | 0% | 36.9243 | 0% | 25.6591 | Storage1 | Li-Ion, 4-hour, 1000 MW | n/a | 85% | 1% | included in CF | n/a | 0 | 0 | 0 | 0
Storage | Gravity Battery, 4-hour, 1000 MW | N/A | 1000 | 2025 | 3 | 2028 | 50 | 2020.9863 | Included in FOM | 0% | 0% | 50.5122 | 0% | 0.19244 | Storage | Gravity Battery, 4-hour, 1000 MW | n/a | 83% | 1% | included in CF | n/a | 0 | 0 | 0 | 0
Storage | Gravity Battery, 4-hour, 1000 MW + Δ Double Duration, Gravity, 4-hour, 1000MW | N/A | 1000 | 2025 | 3 | 2028 | 50 | 3006.3428 | Included in FOM | 0% | 0% | 90.9219 | 0% | 0.3464 | Storage | Gravity Battery, 4-hour, 1000 MW + Δ Double Duration, Gravity, 4-hour, 1000MW | n/a | 83% | 1% | included in CF | n/a | 0 | 0 | 0 | 0
Storage | Adiabatic CAES, 500 MW, 4000 MWh | N/A | 500 | 2025 | 3 | 2028 | 50 | 3754 | 2.6 | 50% | 0% | 19.2 | 42.07% | 49.3111 | Storage | Adiabatic CAES, 500 MW, 4000 MWh | n/a | 62.5% | 1.1% | 1.1% | n/a | 0 | 0 | 0 | 0
Storage | 100-hour Iron Air | N/A | 200 | 2028 | 2 | 2030 | 20 | 2729.6655 | Included in FOM | 0% | 0% | 21.0382 | 19% | 171.061 | Storage | 100-hour Iron Air | n/a | 43% | 1% | included in CF | 0 | 0 | 0 | 0 | 0
Storage | Pumped Hydro, Two New Reservoirs, 4-hour | N/A | 400 | 2025 | 5 | 2030 | 100 | 2984.2304 | 0.58 | 0% | 0% | 20.2 | 45% | 149.2115 | Storage | Pumped Hydro, Two New Reservoirs, 4-hour | n/a | 80% | 2% | 4% | n/a | 0 | 0 | 0 | 0
Storage | Pumped Hydro, Two New Reservoirs, 10-hour | N/A | 400 | 2025 | 5 | 2030 | 100 | 4158.9014 | 0.58 | 0% | 0% | 20.2 | 45% | 207.9451 | Storage | Pumped Hydro, Two New Reservoirs, 10-hour | n/a | 80% | 2% | 4% | n/a | 0 | 0 | 0 | 0
Storage | Pumped Hydro, One New Reservoir, 4-hour | N/A | 400 | 2025 | 5 | 2030 | 100 | 2883.2435 | 0.58 | 0% | 0% | 20.2 | 45% | 144.1622 | Storage | Pumped Hydro, One New Reservoir, 4-hour | n/a | 80% | 2% | 4% | n/a | 0 | 0 | 0 | 0
Storage | Pumped Hydro, One New Reservoir, 10-hour | N/A | 400 | 2025 | 5 | 2030 | 100 | 3537.4133 | 0.58 | 0% | 0% | 20.2 | 45% | 176.8707 | Storage | Pumped Hydro, One New Reservoir, 10-hour | n/a | 80% | 2% | 4% | n/a | 0 | 0 | 0 | 0
Storage | Pumped Thermal Energy Storage, 10-hour | N/A | 100 | 2026 | 5 | 2031 | 60 | 6173.7608 | 0.7 | 0% | 0% | 2 | 0% | 60 | Storage | Pumped Thermal Energy Storage, 10-hour | n/a | 55% | 2% | 3% | n/a | 0 | 0 | 0 | 0
Storage | Pumped Thermal Energy Storage, 24-hour | N/A | 50 | 2026 | 5 | 2031 | 60 | 11525.1739 | 0.7 | 0% | 0% | 1 | 0% | 60 | Storage | Pumped Thermal Energy Storage, 24-hour | n/a | 55% | 2% | 3% | n/a | 0 | 0 | 0 | 0
Solar | PV, 20 MW, Class 1-10 | by location | 20 | 2025 | 3 | 2028 | 25 | 1964.6361 | included in FOM | 0% | 0% | 18.1645 | 12% | 39.2927 | Solar | PV, 20 MW, Class 1-10 | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
Solar | PV, 200 MW, Class 1-10 | by location | 200 | 2025 | 3 | 2028 | 25 | 1216.5527 | included in FOM | 0% | 0% | 20.516 | 12% | 24.3311 | Solar | PV, 200 MW, Class 1-10 | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
Solar | PV, 20 MW, Class 1-10 + Δ Advanced Solar Technology Case | by location | 20 | 2025 | 3 | 2028 | 25 | 1832.2196 | included in FOM | 0% | 0% | 17.24 | 12% | 37.3281 | Solar | PV, 20 MW, Class 1-10 + Δ Advanced Solar Technology Case | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
Solar | PV, 200 MW, Class 1-10 + Δ Advanced Solar Technology Case | by location | 200 | 2025 | 3 | 2028 | 25 | 1134.5571 | included in FOM | 0% | 0% | 19.4717 | 12% | 23.1145 | Solar | PV, 200 MW, Class 1-10 + Δ Advanced Solar Technology Case | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
Wind | Wind Class 1-10, 20 MW | by location | 20 | 2025 | 3 | 2028 | 30 | 2554.5837 | included in FOM | 0% | 0% | 38.7851 | 35% | 63.5725 | Wind | Wind Class 1-10, 20 MW | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
Wind | Wind Class 1-6, 200 MW | by location | 200 | 2025 | 5 | 2030 | 30 | 1421.1042 | included in FOM | 0% | 0% | 31.6482 | 35% | 63.5725 | Wind | Wind Class 1-6, 200 MW | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
Wind | Wind Class 7, 200 MW | by location | 200 | 2025 | 5 | 2030 | 30 | 1491.7767 | included in FOM | 0% | 0% | 31.6482 | 35% | 63.5725 | Wind | Wind Class 7, 200 MW | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
Wind | Offshore, Wind Class 12 | 0 | 200 | 2027 | 5 | 2032 | 30 | 8340.5678 | included in FOM | 0% | 0% | 69.2594 | 35% | 169.1637 | Wind | Offshore, Wind Class 12 | N/A | max CF: 47% | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
Wind | Wind Class 1-10, 20 MW + Δ Advanced Onshore Wind Technology Case | by location | 20 | 2025 | 3 | 2028 | 30 | 2434.2628 | included in FOM | 0% | 0% | 34.8678 | 35% | 60.5783 | Wind | Wind Class 1-10, 20 MW + Δ Advanced Onshore Wind Technology Case | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
Wind | Wind Class 1-6, 200 MW + Δ Advanced Onshore Wind Technology Case | by location | 200 | 2025 | 5 | 2030 | 30 | 1354.1702 | included in FOM | 0% | 0% | 28.4518 | 35% | 60.5783 | Wind | Wind Class 1-6, 200 MW + Δ Advanced Onshore Wind Technology Case | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
Wind | Wind Class 7, 200 MW + Δ Advanced Onshore Wind Technology Case | by location | 200 | 2025 | 5 | 2030 | 30 | 1421.514 | included in FOM | 0% | 0% | 28.4518 | 35% | 60.5783 | Wind | Wind Class 7, 200 MW + Δ Advanced Onshore Wind Technology Case | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
Wind | Offshore, Wind Class 12 + Δ Advanced Offshore Wind Technology Case | 0 | 200 | 2027 | 5 | 2032 | 30 | 6011.0472 | included in FOM | 0% | 0% | 63.213 | 35% | 121.9163 | Wind | Offshore, Wind Class 12 + Δ Advanced Offshore Wind Technology Case | N/A | max CF: 47% | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
1 Assumed co-located | [14 empty] | 1 Assumed co-located
*Assumed co-located

## DB-No Deltas - combined
| Description |  | Resource Characteristics | [5 empty] | Costs | [6 empty] | Operating Characteristics |  |  |  | Environmental
| Fuel | Resource | Elevation (AFSL) | Net Capacity (MW) | Resource Availability Year | Total Implementation Time (yrs) | Commercial Operation Year | Asset Life (yrs) | Base Capital ($/kW) | Var O&M ($/MWh) | Fraction Var O&M Capitalized | Fraction Var O&M Adjusted by Capacity Changes | Fixed O&M ($/kW-yr) | Fraction Fixed O&M Capitalized | Demolition Cost ($/kW) | Average Full Load Heat Rate (HHV Btu/KWh) | Efficiency | EFOR (%) | POR (%) | Water Consumed (Gal/MWh) | SO2 (lbs/MMBtu) | NOx (lbs/MMBtu) | Hg (lbs/TBTu) | CO2 (lbs/MMBtu)
| Biofuel | Internal Combustion Engine, renewable biofuel, with SCR & 24-hour fuel tank | 0 | 20 | 2025 | 2.5 | 2027 | 30 | 2130.9413 | 6.9294 | 74% | 91% | 42.8183 | 3% | 14.5945 | 8295 | 41.13% | 2.5% | 5% | 27.1 | 0.001515 | 0.02 | 0 | 117
| Natural Gas | SCCT Aero, with SCR | 0 | 50 | 2025 | 3.5 | 2028 | 40 | 2612.7968 | 7.4029 | 87% | 98% | 12.4161 | 3% | 32.459 | 9447 | 36.12% | 2.9% | 3.9% | 27 | 0.001504 | 0.0075 | 0 | 117
| Natural Gas | SCCT Aero x4, with SCR | 0 | 211 | 2025 | 3.5 | 2028 | 40 | 1789.352 | 5.9223 | 87% | 98% | 9.9328 | 3% | 32.459 | 9447 | 36.12% | 2.9% | 3.9% | 27 | 0.001504 | 0.0075 | 0 | 117
| Natural Gas | SCCT Frame "F" x1, with SCR | 0 | 233 | 2025 | 5 | 2030 | 40 | 1386.9222 | 7.7513 | 100% | 99% | 27.9225 | 3% | 12.13 | 9717 | 35.12% | 2.7% | 3.9% | 28.4 | 0.001504 | 0.0075 | 0 | 117
| Natural Gas | CCCT Dry "H", 1X1, DF, with SCR | 0 | 649 | 2025 | 5 | 2030 | 40 | 1838.9982 | 2.7029 | 0% | 100% | 42.4422 | 0% | 12.082 | 6040 | 56.49% | 2.5% | 3.8% | 210 | 0.001504 | 0.0075 | 0 | 117
| Natural Gas | CCCT Dry "H", 2X1, DF, with SCR | 0 | 1227 | 2025 | 5 | 2030 | 40 | 1553.2592 | 2.2785 | 0% | 100% | 35.1823 | 0% | 11.886 | 6122 | 55.74% | 2.5% | 3.8% | 210 | 0.001504 | 0.0075 | 0 | 117
| Natural Gas | CCCT Dry "H", 1X1, DF, with SCR + Δ for adding 95% CCS to new CCCT 1x1 | 0 | 565.4765 | 2025 | 5 | 2030 | 40 | 3429.3765 | 5.3164 | 0% | 100% | 77.0661 | 0% | 65.2793 | 6743 | 53.17% | 2.5% | 3.8% | 323.4 | 0.001504 | 0.005625 | 0 | 5.8204
| Natural Gas | CCCT Dry "H", 2X1, DF, with SCR + Δ for adding 95% CCS to new CCCT 2x1 | 0 | 1084.7571 | 2025 | 5 | 2030 | 40 | 2846.0201 | 4.825 | 0% | 100% | 62.9932 | 0% | 65.0833 | 6843 | 52.46% | 2.5% | 3.8% | 323.4 | 0.001504 | 0.005625 | 0 | 5.8204
| Natural Gas | Internal Combustion Engine, renewable biofuel, with SCR & 24-hour fuel tank + Δ for CT Brownfield construction | 0 | 20 | 2025 | 2.5 | 2027 | 30 | 1917.8471 | 6.2364 | 74% | 91% | 42.8183 | 3% | 14.5945 | 8295 | 41.13% | 2.5% | 5% | 27.1 | 0.001515 | 0.02131 | 0 | 117
| Natural Gas | SCCT Aero, with SCR + Δ for CT Brownfield construction | 0 | 50 | 2025 | 3.5 | 2028 | 40 | 2351.5171 | 6.6626 | 87% | 98% | 12.4161 | 3% | 32.459 | 9447 | 36.12% | 2.9% | 3.9% | 27 | 0.001504 | 0.0079913 | 0 | 117
| Natural Gas | SCCT Aero x4, with SCR + Δ for CT Brownfield construction | 0 | 211 | 2025 | 3.5 | 2028 | 40 | 1610.4168 | 5.3301 | 87% | 98% | 9.9328 | 3% | 32.459 | 9447 | 36.12% | 2.9% | 3.9% | 27 | 0.001504 | 0.0079913 | 0 | 117
| Natural Gas | SCCT Frame "F" x1, with SCR + Δ for CT Brownfield construction | 0 | 233 | 2025 | 5 | 2030 | 40 | 1248.23 | 6.9762 | 100% | 99% | 27.9225 | 3% | 12.13 | 9717 | 35.12% | 2.7% | 3.9% | 28.4 | 0.001504 | 0.0079913 | 0 | 117
| Natural Gas | CCCT Dry "H", 1X1, DF, with SCR + Δ for CT Brownfield construction | 0 | 649 | 2025 | 5 | 2030 | 40 | 1655.0984 | 2.4326 | 0% | 100% | 42.4422 | 0% | 12.082 | 6040 | 56.49% | 2.5% | 3.8% | 210 | 0.001504 | 0.0079913 | 0 | 117
| Natural Gas | CCCT Dry "H", 2X1, DF, with SCR + Δ for CT Brownfield construction | 0 | 1227 | 2025 | 5 | 2030 | 40 | 1397.9333 | 2.0506 | 0% | 100% | 35.1823 | 0% | 11.886 | 6122 | 55.74% | 2.5% | 3.8% | 210 | 0.001504 | 0.0079913 | 0 | 117
| Natural Gas | CCCT Dry "H", 1X1, DF, with SCR + Δ for adding 95% CCS to new CCCT 1x1 + Δ for CT Brownfield construction | 0 | 565.4765 | 2025 | 5 | 2030 | 40 | 3086.4388 | 4.7848 | 0% | 100% | 77.0661 | 0% | 65.2793 | 6743 | 53.17% | 2.5% | 3.8% | 323.4 | 0.001504 | 0.0059934 | 0 | 5.8204
| Natural Gas | CCCT Dry "H", 2X1, DF, with SCR + Δ for adding 95% CCS to new CCCT 2x1 + Δ for CT Brownfield construction | 0 | 1084.7571 | 2025 | 5 | 2030 | 40 | 2561.4181 | 4.3425 | 0% | 100% | 62.9932 | 0% | 65.0833 | 6843 | 52.46% | 2.5% | 3.8% | 323.4 | 0.001504 | 0.0059934 | 0 | 5.8204
| Hydrogen | SCCT Frame "F" x1, with SCR + Δ for 100%Hydrogen burning capability | 0 | 233 | 2025 | 5 | 2030 | 40 | 1594.9605 | 8.914 | 100% | 99% | 27.9225 | 3% | 13.9495 | 9717 | 35.12% | 2.7% | 3.9% | 28.4 | 0 | 0.0075 | 0 | 0
| Hydrogen | CCCT Dry "H", 1X1, DF, with SCR + Δ for 100%Hydrogen burning capability | 0 | 649 | 2025 | 5 | 2030 | 40 | 2114.8479 | 3.1083 | 0% | 100% | 42.4422 | 0% | 13.8942 | 6040 | 56.49% | 2.5% | 3.8% | 210 | 0 | 0.0075 | 0 | 0
| Hydrogen | CCCT Dry "H", 2X1, DF, with SCR + Δ for 100%Hydrogen burning capability | 0 | 1227 | 2025 | 5 | 2030 | 40 | 1786.2481 | 2.6202 | 0% | 100% | 35.1823 | 0% | 13.6689 | 6122 | 55.74% | 2.5% | 3.8% | 210 | 0 | 0.0075 | 0 | 0
| Hydrogen | SCCT Frame "F" x1, with SCR + Δ for Hydrogen storage, cavern, 80 bar, 24 hour | 0 | 233 | 2025 | 5 | 2030 | 40 | 2585.9322 | 8.1775 | 100% | 99% | 35.1241 | 3% | 27.13 | 9717 | 35.12% | 2.754% | 3.9% | 28.4 | 0.001962 | 0.009462 | 0.001962 | 0.001962
| Hydrogen | CCCT Dry "H", 1X1, DF, with SCR + Δ for Hydrogen storage, cavern, 80 bar, 24 hour | 0 | 649 | 2025 | 5 | 2030 | 40 | 3038.0082 | 3.1291 | 0% | 100% | 49.6438 | 0% | 27.082 | 6040 | 56.49% | 2.55% | 3.8% | 210 | 0.001962 | 0.009462 | 0.001962 | 0.001962
| Hydrogen | CCCT Dry "H", 2X1, DF, with SCR + Δ for Hydrogen storage, cavern, 80 bar, 24 hour | 0 | 1227 | 2025 | 5 | 2030 | 40 | 2752.2692 | 2.7047 | 0% | 100% | 42.3839 | 0% | 26.886 | 6122 | 55.74% | 2.55% | 3.8% | 210 | 0.001962 | 0.009462 | 0.001962 | 0.001962
| Hydrogen | SCCT Frame "F" x1, with SCR + Δ for Hydrogen storage, tanks, 500 bar, 24 hour | 0 | 233 | 2025 | 5 | 2030 | 40 | 2097.8385 | 8.3231 | 100% | 99% | 40.7792 | 3% | 27.13 | 9717 | 35.12% | 2.754% | 3.9% | 28.4 | 0.001962 | 0.009462 | 0.001962 | 0.001962
| Hydrogen | CCCT Dry "H", 1X1, DF, with SCR + Δ for Hydrogen storage, tanks, 500 bar, 24 hour | 0 | 649 | 2025 | 5 | 2030 | 40 | 2549.9145 | 3.2747 | 0% | 100% | 55.2989 | 0% | 27.082 | 6040 | 56.49% | 2.55% | 3.8% | 210 | 0.001962 | 0.009462 | 0.001962 | 0.001962
| Hydrogen | CCCT Dry "H", 2X1, DF, with SCR + Δ for Hydrogen storage, tanks, 500 bar, 24 hour | 0 | 1227 | 2025 | 5 | 2030 | 40 | 2264.1755 | 2.8502 | 0% | 100% | 48.0391 | 0% | 26.886 | 6122 | 55.74% | 2.55% | 3.8% | 210 | 0.001962 | 0.009462 | 0.001962 | 0.001962
| Natural Gas | CCCT Dry "H", 1X1, DF, with SCR, Advanced Technology Case + Δ advanced technology case, CCCT 1x1 | 0 | 649 | 2025 | 5 | 2030 | 40 | 1831.6324 | 2.6806 | 0% | 100% | 41.3253 | 0% | 12.082 | 6040 | 56.49% | 2.5% | 3.8% | 210 | 0.001504 | 0.0075 | 0 | 117
| Natural Gas | CCCT Dry "H", 2X1, DF, with SCR, Advanced Technology Case + Δ advanced technology case, CCCT 2x1 | 0 | 1227 | 2025 | 5 | 2030 | 40 | 1517.8449 | 2.2338 | 0% | 100% | 34.0654 | 0% | 11.886 | 6122 | 55.74% | 2.5% | 3.8% | 210 | 0.001504 | 0.0075 | 0 | 117
| Natural Gas | CCCT Dry "H", 1X1, DF, with SCR, Advanced Technology Case + Δ advanced technology case, CCCT 1x1 with 95% CCS | 0 | 565.4765 | 2025 | 5 | 2030 | 40 | 3260.8848 | 5.0261 | 0% | 100% | 72.5985 | 0% | 65.2793 | 6743 | 53.17% | 2.5% | 3.8% | 323.4 | 0.001504 | 0.005625 | 0 | 5.8204
| Natural Gas | CCCT Dry "H", 2X1, DF, with SCR, Advanced Technology Case + Δ advanced technology case, CCCT 2x1 with 95% CCS | 0 | 1084.7571 | 2025 | 5 | 2030 | 40 | 2637.1218 | 4.4899 | 0% | 100% | 57.7437 | 0% | 65.0833 | 6843 | 52.46% | 2.5% | 3.8% | 323.4 | 0.001504 | 0.005625 | 0 | 5.8204
| Hydrogen | Electrolyzer, Proton Exchange Membrane (PEM), 50,000 kg/day | 0 | -118.625 | 2025 | 5 | 2030 | 40 | 560.9889 | 23.91 | 0% | 0 | 10.2819 | 100% | 32.459 | N/A | 79.13% | 1.5% | 1.5% | 45.6621 | 0 | 0 | 0 | 0
| Coal | CCS Dave Johnston 4 (costs on post retrofit basis) | 5541 | -84.61 | 2027 | 5 | 2032 | 30 | 3500.7808 | 11.3987 | 0% | 0% | 277.6774 | 0% | 53.1973 | 14794.5994 | 23.06% | 7.5% | 7.5% | 186 | 10 | 0.071 | 0.304 | 10
| Coal | CCS Hunter 1-3 (costs on post retrofit basis) | 6429 | -296.9222 | 2027 | 5 | 2032 | 30 | 2951.2039 | 9.7288 | 0% | 0% | 235.3561 | 0% | 53.1973 | 14011.4943 | 24.35% | 7.5% | 7.5% | 186 | 10 | 0.071 | 0.304 | 10
| Coal | CCS Huntington 1&2 (costs on post retrofit basis) | 6933 | -233.0507 | 2027 | 5 | 2032 | 30 | 2951.3968 | 9.6326 | 0% | 0% | 242.12 | 0% | 53.1973 | 13661.9109 | 24.98% | 7.5% | 7.5% | 186 | 10 | 0.071 | 0.304 | 10
| Coal | CCS Jim Bridger 3&4 (costs on post retrofit basis) | 7513 | -174.3 | 2025 | 5 | 2030 | 30 | 2598.3838 | 10.5675 | 0% | 0% | 254.9074 | 0% | 53.1973 | 14483.2465 | 23.56% | 7.5% | 7.5% | 186 | 10 | 0.071 | 0.304 | 10
| Coal | CCS Wyodak (costs on post retrofit basis) | 4448 | -68.7066 | 2027 | 5 | 2032 | 30 | 3504.2501 | 11.6873 | 0% | 0% | 309.506 | 0% | 53.1973 | 16652.5135 | 20.49% | 7.5% | 7.5% | 186 | 10 | 0.071 | 0.304 | 10
*Assumed co-located | Storage | Li-Ion, 4-hour, 20 MW | N/A | 20 | 2025 | 1 | 2026 | 20 | 1747.6124 | Included in FOM | 0% | 0% | 45.0539 | 0% | 29.9368 | n/a | 85% | 1% | included in CF | n/a | 0 | 0 | 0 | 0
*Assumed co-located | Storage | Li-Ion, 4-hour, 200 MW | N/A | 200 | 2025 | 2 | 2027 | 20 | 1497.8945 | Included in FOM | 0% | 0% | 38.7667 | 0% | 25.6591 | n/a | 85% | 1% | included in CF | n/a | 0 | 0 | 0 | 0
*Assumed co-located | Storage | Li-Ion, 4-hour, 200 MW + Δ Double Duration, Li-Ion, 4-hour, 200MW | N/A | 200 | 2025 | 2 | 2027 | 20 | 2556.5743 | Included in FOM | 0% | 0% | 69.78 | 0% | 46.1865 | n/a | 85% | 1% | included in CF | n/a | 0 | 0 | 0 | 0
*Assumed co-located | Storage | Li-Ion, 4-hour, 1000 MW | N/A | 1000 | 2025 | 3 | 2028 | 20 | 1459.4997 | Included in FOM | 0% | 0% | 36.9243 | 0% | 25.6591 | n/a | 85% | 1% | included in CF | n/a | 0 | 0 | 0 | 0
| Storage | Gravity Battery, 4-hour, 1000 MW | N/A | 1000 | 2025 | 3 | 2028 | 50 | 2020.9863 | Included in FOM | 0% | 0% | 50.5122 | 0% | 0.19244 | n/a | 83% | 1% | included in CF | n/a | 0 | 0 | 0 | 0
| Storage | Gravity Battery, 4-hour, 1000 MW + Δ Double Duration, Gravity, 4-hour, 1000MW | N/A | 1000 | 2025 | 3 | 2028 | 50 | 3006.3428 | Included in FOM | 0% | 0% | 90.9219 | 0% | 0.3464 | n/a | 83% | 1% | included in CF | n/a | 0 | 0 | 0 | 0
| Storage | Adiabatic CAES, 500 MW, 4000 MWh | N/A | 500 | 2025 | 3 | 2028 | 50 | 3754 | 2.6 | 50% | 0% | 19.2 | 42.07% | 49.3111 | n/a | 62.5% | 1.1% | 1.1% | n/a | 0 | 0 | 0 | 0
| Storage | 100-hour Iron Air | N/A | 200 | 2028 | 2 | 2030 | 20 | 2729.6655 | Included in FOM | 0% | 0% | 21.0382 | 19% | 171.061 | n/a | 43% | 1% | included in CF | 0 | 0 | 0 | 0 | 0
| Storage | Pumped Hydro, Two New Reservoirs, 4-hour | N/A | 400 | 2025 | 5 | 2030 | 100 | 2984.2304 | 0.58 | 0% | 0% | 20.2 | 45% | 149.2115 | n/a | 80% | 2% | 4% | n/a | 0 | 0 | 0 | 0
| Storage | Pumped Hydro, Two New Reservoirs, 10-hour | N/A | 400 | 2025 | 5 | 2030 | 100 | 4158.9014 | 0.58 | 0% | 0% | 20.2 | 45% | 207.9451 | n/a | 80% | 2% | 4% | n/a | 0 | 0 | 0 | 0
| Storage | Pumped Hydro, One New Reservoir, 4-hour | N/A | 400 | 2025 | 5 | 2030 | 100 | 2883.2435 | 0.58 | 0% | 0% | 20.2 | 45% | 144.1622 | n/a | 80% | 2% | 4% | n/a | 0 | 0 | 0 | 0
| Storage | Pumped Hydro, One New Reservoir, 10-hour | N/A | 400 | 2025 | 5 | 2030 | 100 | 3537.4133 | 0.58 | 0% | 0% | 20.2 | 45% | 176.8707 | n/a | 80% | 2% | 4% | n/a | 0 | 0 | 0 | 0
| Storage | Pumped Thermal Energy Storage, 10-hour | N/A | 100 | 2026 | 5 | 2031 | 60 | 6173.7608 | 0.7 | 0% | 0% | 2 | 0% | 60 | n/a | 55% | 2% | 3% | n/a | 0 | 0 | 0 | 0
| Storage | Pumped Thermal Energy Storage, 24-hour | N/A | 50 | 2026 | 5 | 2031 | 60 | 11525.1739 | 0.7 | 0% | 0% | 1 | 0% | 60 | n/a | 55% | 2% | 3% | n/a | 0 | 0 | 0 | 0
| Solar | PV, 20 MW, Class 1-10 | by location | 20 | 2025 | 3 | 2028 | 25 | 1964.6361 | included in FOM | 0% | 0% | 18.1645 | 12% | 39.2927 | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
| Solar | PV, 200 MW, Class 1-10 | by location | 200 | 2025 | 3 | 2028 | 25 | 1216.5527 | included in FOM | 0% | 0% | 20.516 | 12% | 24.3311 | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
| Solar | PV, 20 MW, Class 1-10 + Δ Advanced Solar Technology Case | by location | 20 | 2025 | 3 | 2028 | 25 | 1832.2196 | included in FOM | 0% | 0% | 17.24 | 12% | 37.3281 | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
| Solar | PV, 200 MW, Class 1-10 + Δ Advanced Solar Technology Case | by location | 200 | 2025 | 3 | 2028 | 25 | 1134.5571 | included in FOM | 0% | 0% | 19.4717 | 12% | 23.1145 | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
| Wind | Wind Class 1-10, 20 MW | by location | 20 | 2025 | 3 | 2028 | 30 | 2554.5837 | included in FOM | 0% | 0% | 38.7851 | 35% | 63.5725 | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
| Wind | Wind Class 1-6, 200 MW | by location | 200 | 2025 | 5 | 2030 | 30 | 1421.1042 | included in FOM | 0% | 0% | 31.6482 | 35% | 63.5725 | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
| Wind | Wind Class 7, 200 MW | by location | 200 | 2025 | 5 | 2030 | 30 | 1491.7767 | included in FOM | 0% | 0% | 31.6482 | 35% | 63.5725 | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
| Wind | Offshore, Wind Class 12 | 0 | 200 | 2027 | 5 | 2032 | 30 | 8340.5678 | included in FOM | 0% | 0% | 69.2594 | 35% | 169.1637 | N/A | max CF: 47% | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
| Wind | Wind Class 1-10, 20 MW + Δ Advanced Onshore Wind Technology Case | by location | 20 | 2025 | 3 | 2028 | 30 | 2434.2628 | included in FOM | 0% | 0% | 34.8678 | 35% | 60.5783 | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
| Wind | Wind Class 1-6, 200 MW + Δ Advanced Onshore Wind Technology Case | by location | 200 | 2025 | 5 | 2030 | 30 | 1354.1702 | included in FOM | 0% | 0% | 28.4518 | 35% | 60.5783 | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
| Wind | Wind Class 7, 200 MW + Δ Advanced Onshore Wind Technology Case | by location | 200 | 2025 | 5 | 2030 | 30 | 1421.514 | included in FOM | 0% | 0% | 28.4518 | 35% | 60.5783 | N/A | by location | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
| Wind | Offshore, Wind Class 12 + Δ Advanced Offshore Wind Technology Case | 0 | 200 | 2027 | 5 | 2032 | 30 | 6011.0472 | included in FOM | 0% | 0% | 63.213 | 35% | 121.9163 | N/A | max CF: 47% | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a
| Nuclear | Small Modular Reactor or Advanced Reactor, Moderate Technology Case | N/A | 600 | 2030 | 5 | 2035 | 60 | 9662.09 | 9.7419 | 0% | 0% | 97.4192 | 0% | 17 | 9180 | 37.17% | 2% | 5% | 720 | 0 | 0 | 0 | 0
| Nuclear | Small Modular Reactor or Advanced Reactor, Advanced Technology Case | N/A | 600 | 2030 | 4 | 2034 | 60 | 6368.2283 | 8.7391 | 0% | 0% | 84.5255 | 0% | 12 | 9180 | 37.17% | 2% | 5% | 720 | 0 | 0 | 0 | 0
| Nuclear | Small Modular Reactor or Advanced Reactor, Moderate Technology Case + Δ for nuclear integrated thermal storage | N/A | 750 | 2030 | 5 | 2035 | 60 | 10628.299 | 10.7161 | 0% | 0% | 107.1611 | 0% | 17 | 12626.4646 | 37.17% | 2% | 5% | 720 | 0 | 0 | 0 | 0
| Nuclear | Small Modular Reactor or Advanced Reactor, Advanced Technology Case + Δ for nuclear integrated thermal storage | N/A | 750 | 2030 | 4 | 2034 | 60 | 7005.0511 | 9.613 | 0% | 0% | 92.978 | 0% | 12 | 12626.4646 | 37.17% | 2% | 5% | 720 | 0 | 0 | 0 | 0
| Nuclear | Large Light Water Reactor, Moderate Technology Case | N/A | 2000 | 2030 | 7 | 2037 | 60 | 7562.8694 | 9.3838 | 0% | 0% | 125.3556 | 0% | 10 | 10497 | 32.51% | 2% | 5% | 720 | 0 | 0 | 0 | 0
| Nuclear | Large Light Water Reactor, Advanced Technology Case | N/A | 2000 | 2030 | 5 | 2035 | 60 | 6265.2501 | 7.8795 | 0% | 0% | 90.256 | 0% | 9 | 10497 | 32.51% | 2% | 5% | 720 | 0 | 0 | 0 | 0
| Geothermal | Near Field Enhanhanced Geothermal System (NF-EGS) Binary | N/A | 707 | 2025 | 3 | 2028 | 30 | 7593.0583 | included in FOM | 0% | 0% | 194 | 6.074% | 125.0883 | N/A | N/A | 10% | 10% | 510 | n/a | n/a | n/a | n/a
| Geothermal | Near Field Enhanhanced Geothermal System (NF-EGS) Binary + Δ Advanced Geothermal Technology Case | N/A | 707 | 2025 | 3 | 2028 | 30 | 5948.7894 | included in FOM | 0% | 0% | 173.9003 | 6.074% | 125.0883 | N/A | N/A | 10% | 10% | 510 | n/a | n/a | n/a | n/a